## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Providing and fixing flow meter in WTP, Various Hostels and Academics Buildings for IISERTVM Campus
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Providing and fixing Electromagnetic flowmeter as per the specifications complete with bolts,fittings, nuts, rubber insertions,necessary fittings etc. without making damages to the existing lines as per the direction of EIC.Rate including all kind of taxes,fixing charges,loading and unloading chargesand including testing and commisioning Technical Specifications for Electromagnetic Flow meter Fluid : RAW WATER/STP/ETP water Operating Pressure : 3 Bar Operating Temp. : Ambient Electromagnetic Flow Sensor : Line size : 80mm & 100mm Bore Linear Material : PTFE Flow tube : SS Coil housing : MS Electrodes : SS 316 Grounding type : NONE Grounding ring material : NA Process connection : Flanged Flanges : MS | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 1 | Providing and fixing Electromagnetic flowmeter as per the specifications complete with bolts,fittings, nuts, rubber insertions,necessary fittings etc. without making damages to the existing lines as per the direction of EIC.Rate including all kind of taxes,fixing charges,loading and unloading chargesand including testing and commisioning Technical Specifications for Electromagnetic Flow meter Fluid : RAW WATER/STP/ETP water Operating Pressure : 3 Bar Operating Temp. : Ambient Electromagnetic Flow Sensor : Line size : 80mm & 100mm Bore Linear Material : PTFE Flow tube : SS Coil housing : MS Electrodes : SS 316 Grounding type : NONE Grounding ring material : NA Process connection : Flanged Flanges : MS
1.1 | Area Classification : Non-Hazardous Cable entry : M20 x 1.5 with blind plug Protection class : IP 68 Signal Converter Cable length : NA Mounting : Integral Type : Microprocessor Based Output : 4-20m A, RS- 485 Accuracy : ±0.5% of measured value Max load : 500 Ohms Display : Large back lit LCD Display Parameters : Actual flow rate, totalized flow (8 digit), flow direction, flow velocity Diagnostics : Actual flow rate, totalized flow (8 digit), flow direction, flow velocity Local indication : Programmable Power supply : 85-250VAC, 48-63Hz Housing : Die cast Aluminum with Polyester top coat Cable entry : M20 x 1.5 with blind plug Area classification : Non-Hazardous Protection class : IP 66 / 67 Make: ABB,ASTER,FORBES MARSHAL,TOSHNIWAL | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 1.1 | Area Classification : Non-Hazardous Cable entry : M20 x 1.5 with blind plug Protection class : IP 68 Signal Converter Cable length : NA Mounting : Integral Type : Microprocessor Based Output : 4-20m A, RS- 485 Accuracy : ±0.5% of measured value Max load : 500 Ohms Display : Large back lit LCD Display Parameters : Actual flow rate, totalized flow (8 digit), flow direction, flow velocity Diagnostics : Actual flow rate, totalized flow (8 digit), flow direction, flow velocity Local indication : Programmable Power supply : 85-250VAC, 48-63Hz Housing : Die cast Aluminum with Polyester top coat Cable entry : M20 x 1.5 with blind plug Area classification : Non-Hazardous Protection class : IP 66 / 67 Make: ABB,ASTER,FORBES MARSHAL,TOSHNIWAL
1.2 | 100mm |  | 1 | Nos | 404.06 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.2 | 100mm | 1 | Nos
2 | Providing and fixing Analog Water Flow Meter including fixing with necessary materials,supports etc based on the condition of site with out making damages to the existing line etc. all complete as per the direction of EIC. Magnetic Transmission.Rate including all kind of taxes,fixing charges,loading and unloading charges and including testing and commisioning Material of Body : Cast Iron Material of Turbine : Brass Dial : Analog with cover. Working Conditions: Water Pressure: ≤ 1MPa Maximum Pressure: 16 Bar | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 2 | Providing and fixing Analog Water Flow Meter including fixing with necessary materials,supports etc based on the condition of site with out making damages to the existing line etc. all complete as per the direction of EIC. Magnetic Transmission.Rate including all kind of taxes,fixing charges,loading and unloading charges and including testing and commisioning Material of Body : Cast Iron Material of Turbine : Brass Dial : Analog with cover. Working Conditions: Water Pressure: ≤ 1MPa Maximum Pressure: 16 Bar
2.1 | 65mm |  | 11 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.1 | 65mm | 11 | Nos
2.2 | 40 mm |  | 27 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.2 | 40 mm | 27 | Nos
2.3 | 32 mm |  | 26 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.3 | 32 mm | 26 | Nos
2.4 | 25mm |  | 1 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.4 | 25mm | 1 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information