## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work:Supply and installation of self-supported roof in Kabaddi court near Indoor stadium at IISER campus, Vithura
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply, Installation, Testing & Commissioning of chlorine control system into the existing 4" line without damageing the existing line (detailed specification and work details are enclosed)(rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 1 | Supply, Installation, Testing & Commissioning of chlorine control system into the existing 4" line without damageing the existing line (detailed specification and work details are enclosed)(rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC)
1.1 | Sodium Hypochlorite Dosing pump Quantity-1Nos Capacity 6LPH @ 4bar backpressure Type Plasma Diaphragm type metering pumps MOC :PP Make : Milton Roy/Prominent Tank 1Nos, 100L Residual Chlorine Analyzer 1Nos Type Amperometric IP 67 Make: Prominent/Milton Roy (rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC) |  | 1 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.1 | Sodium Hypochlorite Dosing pump Quantity-1Nos Capacity 6LPH @ 4bar backpressure Type Plasma Diaphragm type metering pumps MOC :PP Make : Milton Roy/Prominent Tank 1Nos, 100L Residual Chlorine Analyzer 1Nos Type Amperometric IP 67 Make: Prominent/Milton Roy (rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC) | 1 | Nos
2 | Supply, Installation, Testing & Commissioning of pH Monitoring unit into the existing 4" line without damageing the existing line(detailed specification and work details are enclosed, (rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC)) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 2 | Supply, Installation, Testing & Commissioning of pH Monitoring unit into the existing 4" line without damageing the existing line(detailed specification and work details are enclosed, (rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC))
2.1 | pH meter with sensor Qty 1 set Range 1 - 7 Display LCD Make :Aster/E dose |  | 1 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.1 | pH meter with sensor Qty 1 set Range 1 - 7 Display LCD Make :Aster/E dose | 1 | Nos
3 | Supply, Installation, Testing & Commissioning of Static Mixer (detailed specification and work details are enclosed,(rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC)) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 3 | Supply, Installation, Testing & Commissioning of Static Mixer (detailed specification and work details are enclosed,(rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC))
3.1 | Qty 1 Nos MOC SS316 End connection Flanged Length 500mm |  | 1 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3.1 | Qty 1 Nos MOC SS316 End connection Flanged Length 500mm | 1 | Nos
4 | Supply, Installation, Testing & Commissioning of UV system including providing 4 Nos. 4" butterfly valve etc as per the direction of EIC into the existing system (detailed specification and work details are enclosed,rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC) | [6 empty] | Excess(+) | 1 | Full Conversion | INR | [43 empty] | 4 | Supply, Installation, Testing & Commissioning of UV system including providing 4 Nos. 4" butterfly valve etc as per the direction of EIC into the existing system (detailed specification and work details are enclosed,rate inclusive of all fittings,alternation works, new piping if required as per site conditions etc as per direction of EIC)
4.1 | Design Flow rate : 70.0m3/hr UVDose(@EOL) 30mJ/cm2 UVTransmission(percm) 95% MOC Stainless Steel 316L Make Alfa End Connections 4.0"Flange(BS10) MaximumOperating Pressure 80 psi RecommendedWater Temperature 18° - 45° Celsius MaximumSanitization Temperature 85° C (lamps turned off) O-ringsandSeals MOC FoodGrade EPDM (as per US FDA 21 CFR 177.2600) QuartzJacket MOC High Purity Quartz (UVT> 95%) Voltage 220-240V/50-60 Hz MaximumPower Consumption 733W MaximumLampCable Length 4.5 m System Rating For Indoor Use Only UVLampFailure Indication Included UVLampHourRun Counter Included Contractor has to submit the one month water test result from approved lab for releasing the final payment |  | 1 | Nos | 2769.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | Design Flow rate : 70.0m3/hr UVDose(@EOL) 30mJ/cm2 UVTransmission(percm) 95% MOC Stainless Steel 316L Make Alfa End Connections 4.0"Flange(BS10) MaximumOperating Pressure 80 psi RecommendedWater Temperature 18° - 45° Celsius MaximumSanitization Temperature 85° C (lamps turned off) O-ringsandSeals MOC FoodGrade EPDM (as per US FDA 21 CFR 177.2600) QuartzJacket MOC High Purity Quartz (UVT> 95%) Voltage 220-240V/50-60 Hz MaximumPower Consumption 733W MaximumLampCable Length 4.5 m System Rating For Indoor Use Only UVLampFailure Indication Included UVLampHourRun Counter Included Contractor has to submit the one month water test result from approved lab for releasing the final payment | 1 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information