## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Electrical works for providing lights in New Kho-Kho court in IISER TVM campus Vithura , Thiruvananthapuram (Part-1 Supply and installation of poles, lightfittings and its associated works)
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Basic unit Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply,installation, testing and commissioning of 9Mtr long GI octogonal/conical pole made of MS steel having having neccesary sections if required as per manufactures design with suitable base plate and necessary single arm each ,min sheet steel thickness 3mm ,suitable for providing 4 Nos 27500 Lumens LED fittings, and all materials required for installation like interconnecting cable with 2Runs of 3C 2.5 sq.mm FR PVC insulated stranded copper conductor flexible cable , bolts, nuts, DIN rail, 16A SP MCB-2 Nos, 32A connectors heavy duty 4way, N.L-2Nos, 3mm thick laminated hylem sheet, Pole earthing, glanding in 3 mm thick M.S. sheet includings connection complete as required and all related works as directed by the EIC. (Pole-Crompton/Bajaj/Klite or Equivalent to suit the existing foundation) |  | 4 | Each | 31196 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply,installation, testing and commissioning of 9Mtr long GI octogonal/conical pole made of MS steel having having neccesary sections if required as per manufactures design with suitable base plate and necessary single arm each ,min sheet steel thickness 3mm ,suitable for providing 4 Nos 27500 Lumens LED fittings, and all materials required for installation like interconnecting cable with 2Runs of 3C 2.5 sq.mm FR PVC insulated stranded copper conductor flexible cable , bolts, nuts, DIN rail, 16A SP MCB-2 Nos, 32A connectors heavy duty 4way, N.L-2Nos, 3mm thick laminated hylem sheet, Pole earthing, glanding in 3 mm thick M.S. sheet includings connection complete as required and all related works as directed by the EIC. (Pole-Crompton/Bajaj/Klite or Equivalent to suit the existing foundation) | 4 | Each
2 | Supply of high-quality integrated LED Flood Light with a minimum system lumen of 44000 Lm and system wattage not more than 400 W with a nominal efficiency 110 lumen/watt (min) using High power LED's, with integrated Peanut Lens shall be mounted on each LED by injection moulding process on PC Cover . The housing should be of non-corrosive high-pressure die-cast aluminum alloy to with stand extreme environments, should have corrosion resistant coating .The Luminaire should be having Minimum 50000 Burning hours(L70B50) with CRI ≥70 and co-related color temperature (CCT) of 5700K with assymetric/ suitable beam angle. The Ingress protection must be minimum IP 66 with an IK rating of 08. LED used in the luminaire shall be of make of Lumileds, Osram, Nichia, Seoul and CREE & no other make. The Luminaire should have a 10 KV SPD duly bolted in the Luminaire . The luminaire shall be flicker free with a ripple content less than 10 %. the luminare should have PF>0.95 and THD<10%.Luminaire and driver shall be separately BIS approved of same make. Make: Wipro Cat Ref LF20-502-060-57-G4/Philips BVP485 LED 485 CW AWB PSU SPD GR or Equivlent. Led lightfittings have 5years onsite warranty. Equivalent make shall submit dialux report and technical data sheet for approval. |  | 16 | Each | 35104 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Supply of high-quality integrated LED Flood Light with a minimum system lumen of 44000 Lm and system wattage not more than 400 W with a nominal efficiency 110 lumen/watt (min) using High power LED's, with integrated Peanut Lens shall be mounted on each LED by injection moulding process on PC Cover . The housing should be of non-corrosive high-pressure die-cast aluminum alloy to with stand extreme environments, should have corrosion resistant coating .The Luminaire should be having Minimum 50000 Burning hours(L70B50) with CRI ≥70 and co-related color temperature (CCT) of 5700K with assymetric/ suitable beam angle. The Ingress protection must be minimum IP 66 with an IK rating of 08. LED used in the luminaire shall be of make of Lumileds, Osram, Nichia, Seoul and CREE & no other make. The Luminaire should have a 10 KV SPD duly bolted in the Luminaire . The luminaire shall be flicker free with a ripple content less than 10 %. the luminare should have PF>0.95 and THD<10%.Luminaire and driver shall be separately BIS approved of same make. Make: Wipro Cat Ref LF20-502-060-57-G4/Philips BVP485 LED 485 CW AWB PSU SPD GR or Equivlent. Led lightfittings have 5years onsite warranty. Equivalent make shall submit dialux report and technical data sheet for approval. | 16 | Each
3 | Installation, testing and commissioning of LED type flood light luminaries up to 400 W with mounting bracket etc as required in existing 9 m pole includings required accessories,connection complete as required and all related works as directed by the EIC . |  | 16 | Each | 530 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Installation, testing and commissioning of LED type flood light luminaries up to 400 W with mounting bracket etc as required in existing 9 m pole includings required accessories,connection complete as required and all related works as directed by the EIC . | 16 | Each
4 | Supply and making end termination with brass compression gland with gland earthing and aluminium lugs for following size of PVC insulated and PVC sheathed /XLPE Al. conductor cable of 1.1 KV grade as required. | [53 empty] | 4 | Supply and making end termination with brass compression gland with gland earthing and aluminium lugs for following size of PVC insulated and PVC sheathed /XLPE Al. conductor cable of 1.1 KV grade as required.
4.1 | 4 x 6 Sqmm |  | 2 | Each | 229 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | 4 x 6 Sqmm | 2 | Each
4.2 | 4 x 4 Sqmm |  | 8 | Each | 190 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.2 | 4 x 4 Sqmm | 8 | Each
5 | Supply and fixing of following ways surface/ recess mounting, single pole and neutral, outdoor type IP-65 whether proof MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | [53 empty] | 5 | Supply and fixing of following ways surface/ recess mounting, single pole and neutral, outdoor type IP-65 whether proof MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
5.1 | 12 way |  | 1 | Each | 3999 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.1 | 12 way | 1 | Each
6 | Fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | [53 empty] | 6 | Fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
6.1 | Single Pole |  | 4 | Each | 79 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6.1 | Single Pole | 4 | Each
7 | Fixing, testing and commissioning of following rating RCBO or MCCB as required in existing vertical distribution board including drilling holes in the vertical distribution board, making connections etc as required at incomer. | [53 empty] | 7 | Fixing, testing and commissioning of following rating RCBO or MCCB as required in existing vertical distribution board including drilling holes in the vertical distribution board, making connections etc as required at incomer.
7.1 | Upto 63A DP RCBO/MCB |  | 1 | Each | 99 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.1 | Upto 63A DP RCBO/MCB | 1 | Each
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information