## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: External lighting in children's park and around the walk way near Residence area at IISER campus, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Basic unit Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply, installation, testing and commissioning of pre-wired LED post top lanterns consisting of lumen level not less than 3500lumens and not more than 41W power, the fixture should be powder coated diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 3000K warm white,min 6KV surge protection, IP65 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required.The light fixture should have 2 year on site warranty. (Approved makes: Philips BDP102 LED50/830 DS PCC GR MSP 62P,Schederer Cat No. ZELA 37W WW, Wipro Led LP07 -431) |  | 21 | Each | 7817.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply, installation, testing and commissioning of pre-wired LED post top lanterns consisting of lumen level not less than 3500lumens and not more than 41W power, the fixture should be powder coated diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 3000K warm white,min 6KV surge protection, IP65 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required.The light fixture should have 2 year on site warranty. (Approved makes: Philips BDP102 LED50/830 DS PCC GR MSP 62P,Schederer Cat No. ZELA 37W WW, Wipro Led LP07 -431) | 21 | Each
2 | Supply and fixing of 4meter long conical pole on pole foundation with inspection door,fully galvanised M16X600mm foundation bolts, including earth excavation, providing RCC pedestal 400mm x 400mm x 1100mm size (200mm above the ground level and 900mm below the ground level) or as per pole manufacturer's recommendation,6A DP MCB , interconnecting flexible cable of size 3core x 1.5sqmm , terminal block and looping, Earthing etc. complete as required and painting with epoxy primer and aluminium paint complete as required and as directed by Engineer in charge. Note: The street light pole should be suitable for the light fixture as mentioned in item no.1.0. The pole should be factory fabricated from reputed manufacturer |  | 21 | Each | 20359.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Supply and fixing of 4meter long conical pole on pole foundation with inspection door,fully galvanised M16X600mm foundation bolts, including earth excavation, providing RCC pedestal 400mm x 400mm x 1100mm size (200mm above the ground level and 900mm below the ground level) or as per pole manufacturer's recommendation,6A DP MCB , interconnecting flexible cable of size 3core x 1.5sqmm , terminal block and looping, Earthing etc. complete as required and painting with epoxy primer and aluminium paint complete as required and as directed by Engineer in charge. Note: The street light pole should be suitable for the light fixture as mentioned in item no.1.0. The pole should be factory fabricated from reputed manufacturer | 21 | Each
3 | Supply of one number XLPE power cable of 1.1 kV grade of following size as required. | [53 empty] | 3 | Supply of one number XLPE power cable of 1.1 kV grade of following size as required.
3.1 | 2C x 4 sqmm Aluminium armoured cable |  | 330 | Metre | 100.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3.1 | 2C x 4 sqmm Aluminium armoured cable | 330 | Metre
4 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required | [53 empty] | 4 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required
4.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) |  | 15 | Metre | 48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 15 | Metre
5 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | [53 empty] | 5 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
5.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) |  | 360 | Metre | 256 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 360 | Metre
6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade size upto 35sqmm in the existing RCC/ HUME/ METAL/HDPE pipe as required. |  | 360 | Metre | 38 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade size upto 35sqmm in the existing RCC/ HUME/ METAL/HDPE pipe as required. | 360 | Metre
7 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required. | [53 empty] | 7 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required.
7.1 | 2core X 4 sq. mm (19mm) |  | 42 | Each | 243 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.1 | 2core X 4 sq. mm (19mm) | 42 | Each
7.2 | 4core X 25 sq. mm (28mm) |  | 2 | Each | 307 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.2 | 4core X 25 sq. mm (28mm) | 2 | Each
8 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required |  | 448 | meter | 58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 8 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required | 448 | meter
9 | Supply and installation of weather proof thermoplastic enclosure of size 530mm x 450mm x 175mm complete with DIN rails,suitable connectors etc. mounted on floor using angle iron support of size 40mmx 40mmx 6mm as required and as directed by Engineer in charge |  | 1 | Each | 3883.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 9 | Supply and installation of weather proof thermoplastic enclosure of size 530mm x 450mm x 175mm complete with DIN rails,suitable connectors etc. mounted on floor using angle iron support of size 40mmx 40mmx 6mm as required and as directed by Engineer in charge | 1 | Each
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information