## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Electrical works at The School of Earth Environment and Sustainability Science Building at IISER, Thiruvananthapuram
Contact No: 0471-2778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Basic unit Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. (switch and cover plate for UPS lighting shall be in black colour) GroupC |  | 39 | Point | 1467 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. (switch and cover plate for UPS lighting shall be in black colour) GroupC | 39 | Point
2 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required. | [53 empty] | 2 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required.
2.1 | 2 x 2.5 sq.mm + 1 x 2.5 sq.mm earth wire |  | 405 | metre | 275 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.1 | 2 x 2.5 sq.mm + 1 x 2.5 sq.mm earth wire | 405 | metre
2.2 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire |  | 1171 | metre | 334 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.2 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire | 1171 | metre
2.3 | 4 x 6 sq.mm + 2 x 6 sq.mm earth wire |  | 75 | metre | 754 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.3 | 4 x 6 sq.mm + 2 x 6 sq.mm earth wire | 75 | metre
2.4 | 4 x 16 sq.mm + 2x 6 sq.mm earth wire (For Raw Power DB) |  | 32 | metre | 1365 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.4 | 4 x 16 sq.mm + 2x 6 sq.mm earth wire (For Raw Power DB) | 32 | metre
3 | Supplying and fixing following size/modules, GI box for modular switches in recess etc as required. | [53 empty] | 3 | Supplying and fixing following size/modules, GI box for modular switches in recess etc as required.
3.1 | 2 Module |  | 59 | Each | 232.07 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.1 | 2 Module | 59 | Each
3.2 | 3 Module |  | 35 | Each | 242.67 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.2 | 3 Module | 35 | Each
3.3 | 6 Module |  | 41 | Each | 286.38 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.3 | 6 Module | 41 | Each
3.4 | 8 Module |  | 39 | Each | 307.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.4 | 8 Module | 39 | Each
4 | Supplying and fixing following modular base & cover plate on exisitng modular metal boxes as required. | [53 empty] | 4 | Supplying and fixing following modular base & cover plate on exisitng modular metal boxes as required.
4.1 | 1 Module (white) |  | 53 | Each | 133 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.1 | 1 Module (white) | 53 | Each
4.2 | 2 Module (white) |  | 10 | Each | 133 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.2 | 2 Module (white) | 10 | Each
4.3 | 3 Module (Black) |  | 15 | Each | 293.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.3 | 3 Module (Black) | 15 | Each
4.4 | 3 Module (white) |  | 22 | Each | 151 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.4 | 3 Module (white) | 22 | Each
4.5 | 6 Module (Black) |  | 35 | Each | 494.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.5 | 6 Module (Black) | 35 | Each
4.6 | 6 Module (white) |  | 6 | Each | 182 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.6 | 6 Module (white) | 6 | Each
4.7 | 8 Module (Black) |  | 35 | Each | 542.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.7 | 8 Module (Black) | 35 | Each
4.8 | 8 Module (white) |  | 4 | Each | 211 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.8 | 8 Module (white) | 4 | Each
5 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate & swich box etc as required. | [53 empty] | 5 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate & swich box etc as required.
5.1 | 5/6A switch (Black) |  | 98 | Each | 156.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.1 | 5/6A switch (Black) | 98 | Each
5.2 | 5/6A switch (white) |  | 23 | Each | 103 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.2 | 5/6A switch (white) | 23 | Each
5.3 | 3pin 5/6A socket (Black) |  | 112 | Each | 200.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.3 | 3pin 5/6A socket (Black) | 112 | Each
5.4 | 3pin 5/6A socket (white) |  | 46 | Each | 122 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.4 | 3pin 5/6A socket (white) | 46 | Each
5.5 | 15/16A switch (Black) |  | 55 | Each | 251.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.5 | 15/16A switch (Black) | 55 | Each
5.6 | 15/16A switch (white) |  | 24 | Each | 156 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.6 | 15/16A switch (white) | 24 | Each
5.7 | 6 pin 15/16A socket (Black) |  | 55 | Each | 360.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.7 | 6 pin 15/16A socket (Black) | 55 | Each
5.8 | 6 pin 15/16A socket (white) |  | 24 | Each | 197 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.8 | 6 pin 15/16A socket (white) | 24 | Each
5.9 | RJ 45 Data socket (white) |  | 65 | Each | 500.78 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5.9 | RJ 45 Data socket (white) | 65 | Each
6 | Installation of 4/8/12Way surface/recess mounting , vertical type, 415 V, TPN MCB distribution board of sheet steel,for mounting MCBs as incomer & outgoings as required and as directed by Engineer incharge but without MCBs. (Legrand make DB shall be issued by the Department; all other materials like steel fastener, cement, paint, sand etc. to complete the work in all respect shall be the scope of contractor.) |  | 2 | Each | 612 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6 | Installation of 4/8/12Way surface/recess mounting , vertical type, 415 V, TPN MCB distribution board of sheet steel,for mounting MCBs as incomer & outgoings as required and as directed by Engineer incharge but without MCBs. (Legrand make DB shall be issued by the Department; all other materials like steel fastener, cement, paint, sand etc. to complete the work in all respect shall be the scope of contractor.) | 2 | Each
7 | Installation of 4/8/12Way surface/recess mounting , Vertical type, 415 V, 160A TPN MCCB distribution board of sheet steel,for mounting MCCB as incomer and MCBs as outgoings and as required & directed by Engineer incharge but without MCCB & MCBs. (Legrand make DB shall be issued by the Department; all other materials like steel fastener, cement, paint, sand etc. to complete the work in all respect shall be the scope of contractor.) |  | 1 | Each | 756 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7 | Installation of 4/8/12Way surface/recess mounting , Vertical type, 415 V, 160A TPN MCCB distribution board of sheet steel,for mounting MCCB as incomer and MCBs as outgoings and as required & directed by Engineer incharge but without MCCB & MCBs. (Legrand make DB shall be issued by the Department; all other materials like steel fastener, cement, paint, sand etc. to complete the work in all respect shall be the scope of contractor.) | 1 | Each
8 | Supplying and fixing 5A to 32A rating, 240V, 10kA, "D" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand |  | 72 | Each | 399 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 8 | Supplying and fixing 5A to 32A rating, 240V, 10kA, "D" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand | 72 | Each
9 | Supplying and fixing 63A rating, 415V, 10kA, "D" curvefollowing pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Make : Legrand | [53 empty] | 9 | Supplying and fixing 63A rating, 415V, 10kA, "D" curvefollowing pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Make : Legrand
9.1 | Three pole |  | 8 | Each | 2091 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 9.1 | Three pole | 8 | Each
9.2 | Four pole |  | 2 | Each | 2634 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 9.2 | Four pole | 2 | Each
10 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. |  | 12 | Each | 13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 10 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | 12 | Each
11 | Supplying and fixing following rating four pole 415V RCCB having sensitivity current 100mA with model satisfying enhanced immunity to unwanted tripping in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand | [53 empty] | 11 | Supplying and fixing following rating four pole 415V RCCB having sensitivity current 100mA with model satisfying enhanced immunity to unwanted tripping in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand
11.1 | 63A |  | 2 | Each | 6715 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 11.1 | 63A | 2 | Each
12 | Supplying and fixing DP sheet steel enclosure on surface/recess along with 25/32A 240V "D" curve DP MCB complete with connections, testing and commissioning etc as required. |  | 2 | Each | 1366 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 12 | Supplying and fixing DP sheet steel enclosure on surface/recess along with 25/32A 240V "D" curve DP MCB complete with connections, testing and commissioning etc as required. | 2 | Each
13 | Supplying and fixing 4P sheet steel enclosure on surface/recess along with 25/32A 415V "D" curve 4P MCB complete with connections, testing and commissioning etc as required. |  | 1 | Each | 2438 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 13 | Supplying and fixing 4P sheet steel enclosure on surface/recess along with 25/32A 415V "D" curve 4P MCB complete with connections, testing and commissioning etc as required. | 1 | Each
14 | Supplying and fixing DP IP65 enclosure on surface/recess along with 25/32A 240V "D" curve DP MCB complete with connections, testing and commissioning etc as required. (Enclosure Make : Legrand Plexo box or equivalent for Schneider/Hager) |  | 2 | Each | 2274 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 14 | Supplying and fixing DP IP65 enclosure on surface/recess along with 25/32A 240V "D" curve DP MCB complete with connections, testing and commissioning etc as required. (Enclosure Make : Legrand Plexo box or equivalent for Schneider/Hager) | 2 | Each
15 | Supplying and fixing 4P IP65 enclosure on surface/recess along with 25/32A 415V "D" curve 4P MCB complete with connections, testing and commissioning etc as required. (Enclosure Make : Legrand Plexo box or equivalent for Schneider/Hager) |  | 1 | Each | 3242 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 15 | Supplying and fixing 4P IP65 enclosure on surface/recess along with 25/32A 415V "D" curve 4P MCB complete with connections, testing and commissioning etc as required. (Enclosure Make : Legrand Plexo box or equivalent for Schneider/Hager) | 1 | Each
16 | Providing and fixing 160A 16kA 4P MCCB with thermal magnetc release and terminal spreaders in exising VDB including making connections aetc as required. Make : Legrand |  | 1 | Each | 8548 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 16 | Providing and fixing 160A 16kA 4P MCCB with thermal magnetc release and terminal spreaders in exising VDB including making connections aetc as required. Make : Legrand | 1 | Each
17 | Supplying and installing following size of perforated HDGI cable tray (Galvanization not less than 50microns) with perforation not more than 17.5% in convenient sections, joined with connectors, bends etc clamped on wall/suspended fro the ceiling with GI suspenders including GI bolts & nuts etc as required. (Tray for cable drop to panel is also included) (For Electrical & ELV) | [53 empty] | 17 | Supplying and installing following size of perforated HDGI cable tray (Galvanization not less than 50microns) with perforation not more than 17.5% in convenient sections, joined with connectors, bends etc clamped on wall/suspended fro the ceiling with GI suspenders including GI bolts & nuts etc as required. (Tray for cable drop to panel is also included) (For Electrical & ELV)
17.1 | 225mm width x 50mm depth x 1.6mm thickness |  | 20 | metre | 895 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 17.1 | 225mm width x 50mm depth x 1.6mm thickness | 20 | metre
17.2 | 150mm width x 50mm depth x 1.6mm thickness |  | 80 | metre | 716 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 17.2 | 150mm width x 50mm depth x 1.6mm thickness | 80 | metre
18 | Supply of following XLPE insulated FRLS power cable of 1.1kV grade of following size as required. | [53 empty] | 18 | Supply of following XLPE insulated FRLS power cable of 1.1kV grade of following size as required.
18.1 | 4Cx150Sq.mm Ar. Al XLPE FRLS cable |  | 15 | metre | 1681 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 18.1 | 4Cx150Sq.mm Ar. Al XLPE FRLS cable | 15 | metre
18.2 | 4Cx50Sq.mm Ar. Al XLPE FRLS cable |  | 8 | metre | 681 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 18.2 | 4Cx50Sq.mm Ar. Al XLPE FRLS cable | 8 | metre
18.3 | 4Cx25Sq.mm Ar. Al XLPE FRLS cable |  | 80 | metre | 399 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 18.3 | 4Cx25Sq.mm Ar. Al XLPE FRLS cable | 80 | metre
18.4 | 1Cx70Sq.mm Un Ar. Cu XLPE FRLS cable |  | 62 | metre | 114 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 18.4 | 1Cx70Sq.mm Un Ar. Cu XLPE FRLS cable | 62 | metre
19 | Supply of following XLPE insulated FRLS power cable of 1.1kV grade of following size as required. | [53 empty] | 19 | Supply of following XLPE insulated FRLS power cable of 1.1kV grade of following size as required.
19.1 | Laying and fixing of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1kV grade of following size on cable tray as required. |  | 15 | metre | 115 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 19.1 | Laying and fixing of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1kV grade of following size on cable tray as required. | 15 | metre
19.2 | Above 95sq.mm and upto 185sq.mm (clamped with 25/40x3mm MS flat clamp) |  | 70 | metre | 92 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 19.2 | Above 95sq.mm and upto 185sq.mm (clamped with 25/40x3mm MS flat clamp) | 70 | metre
19.3 | Above 35sq.mm and upto 95sq.mm (clamped with 25x3mm MS flat clamp) |  | 80 | metre | 45 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 19.3 | Above 35sq.mm and upto 95sq.mm (clamped with 25x3mm MS flat clamp) | 80 | metre
20 | Supplying and making end termination with gland and lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required. Make : Dowells/Jainson | [53 empty] | 20 | Supplying and making end termination with gland and lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required. Make : Dowells/Jainson
20.1 | 4Cx150Sq.mm Ar. Al XLPE FRLS cable (with brass cmpression gland and aluminium lugs) |  | 2 | Each | 711 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 20.1 | 4Cx150Sq.mm Ar. Al XLPE FRLS cable (with brass cmpression gland and aluminium lugs) | 2 | Each
20.2 | 4Cx50Sq.mm Ar. Al XLPE FRLS cable (with brass cmpression gland and aluminium lugs) |  | 2 | Each | 418 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 20.2 | 4Cx50Sq.mm Ar. Al XLPE FRLS cable (with brass cmpression gland and aluminium lugs) | 2 | Each
20.3 | 4Cx25Sq.mm Ar. Al XLPE FRLS cable (with brass cmpression gland and aluminium lugs) |  | 4 | Each | 315 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 20.3 | 4Cx25Sq.mm Ar. Al XLPE FRLS cable (with brass cmpression gland and aluminium lugs) | 4 | Each
20.4 | 1Cx70Sq.mm Un Ar. Cu XLPE FRLS cable (with Nylon PG gland and copper lugs) |  | 16 | Each | 347 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 20.4 | 1Cx70Sq.mm Un Ar. Cu XLPE FRLS cable (with Nylon PG gland and copper lugs) | 16 | Each
21 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. |  | 2 | Each | 13838 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 21 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2 | Each
22 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) |  | 15 | metre | 972 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 22 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 15 | metre
23 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required |  | 40 | metre | 1162 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 23 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required | 40 | metre
24 | Providing and fixing 4.00mm dia copper wire on surface or in recess for loop earthing as required |  | 45 | metre | 155 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 24 | Providing and fixing 4.00mm dia copper wire on surface or in recess for loop earthing as required | 45 | metre
25 | Supply, installation,testing and commissioning of online IGBT based double conversion transformer free modular UPS of capacity 75 KVA(N+1 redundancy module) having expandable frame size of minumum 125kVA,three phase input, 415 Volts ±15%, 50±3 Hz, and three phase output 415 Volt ± 1%, 50 Hz, sinusoidal waveform , ,efficiency > 96% at 25% to 100% of load, automatic UPS bypass arrangement on overload or UPS failure, capable to handle overload of 125% for minimum 1 minutes and 150% for minimum 10sec, with network and modbus card to monitor the operation of UPS, IP 20 or more rated cabinet,built in dust filter, suitable ventilation arrangement, suitable capacity battery circuit breaker, AC/DC power and control cables, other accessories set as per Technical Specifications. Note: 1. UPS shall be compatible for 2 string battery banks 2. UPS should be IGBT based Rectifier and IGBT based Inverter 3. The UPS should be N+1 modular, incase of failure of one module, the remaining modules should catering the load. 4. UPS shall be latest batch not older than 6 months from the date of manufacturing 5. Warranty : 5 years 6. Make: Vertiv/Eaton/Legrand(Numeric) |  | 1 | Each | 1741680 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 25 | Supply, installation,testing and commissioning of online IGBT based double conversion transformer free modular UPS of capacity 75 KVA(N+1 redundancy module) having expandable frame size of minumum 125kVA,three phase input, 415 Volts ±15%, 50±3 Hz, and three phase output 415 Volt ± 1%, 50 Hz, sinusoidal waveform , ,efficiency > 96% at 25% to 100% of load, automatic UPS bypass arrangement on overload or UPS failure, capable to handle overload of 125% for minimum 1 minutes and 150% for minimum 10sec, with network and modbus card to monitor the operation of UPS, IP 20 or more rated cabinet,built in dust filter, suitable ventilation arrangement, suitable capacity battery circuit breaker, AC/DC power and control cables, other accessories set as per Technical Specifications. Note: 1. UPS shall be compatible for 2 string battery banks 2. UPS should be IGBT based Rectifier and IGBT based Inverter 3. The UPS should be N+1 modular, incase of failure of one module, the remaining modules should catering the load. 4. UPS shall be latest batch not older than 6 months from the date of manufacturing 5. Warranty : 5 years 6. Make: Vertiv/Eaton/Legrand(Numeric) | 1 | Each
26 | Supply, installation , testing and commissioning of two battery banks (one redundancy) of suitable capacity 12Volt VRLA battery to provide 15minutes backup at full load for the UPS as specified in item no. 25 with battery racks made up of metal channels to place above batteries, cables, fusebox and required switchgear to operate battery banks in parallel in complete. Note: 1. Battery sizing shall be based on Unity Power Factor and cut off voltage 10.5 V 2. Suitable links,required accessories to be provided, painting of the stand, 3. Batteries shall be in full charged condition and latest batch not older than 6 months from the date of manufacturing 4. Batteries make: Quanta-Amaron 5. Warranty : As per manufacturer warranty |  | 2 | sets | 269690 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 26 | Supply, installation , testing and commissioning of two battery banks (one redundancy) of suitable capacity 12Volt VRLA battery to provide 15minutes backup at full load for the UPS as specified in item no. 25 with battery racks made up of metal channels to place above batteries, cables, fusebox and required switchgear to operate battery banks in parallel in complete. Note: 1. Battery sizing shall be based on Unity Power Factor and cut off voltage 10.5 V 2. Suitable links,required accessories to be provided, painting of the stand, 3. Batteries shall be in full charged condition and latest batch not older than 6 months from the date of manufacturing 4. Batteries make: Quanta-Amaron 5. Warranty : As per manufacturer warranty | 2 | sets
27 | Supplying, fabrication, installation,testing and commissioing of cubicle type prewired LT Panel suitable for 415 Volt, 3 phase, 4 wire 50 HZ AC supply system, floor mounted, fabricated in compartmentalized design from CRCA steel of 1.6 mm thick for frame work and covers, 3 mm thick for gland plates, including finishing with powder coated, dust and vermin proof complete with 7 tank process having extensible type aluminium bus bar with full rated neutral of high conductivity ,3 mm FRP / SMC Sheet for shrouding, base frame of M.S. channel section of not less than 75 mm x 40 mmx6mm thick, copper earth bar of size 25mmx 5mm or at the rear with 2 No. earth stud, complete with 1.5sqmm FRLS PVC insulated copper conducter for control wires, cable alleys, cable gland plates, including following : All MCCB shall have ICu =100% ICs MCCB shall be operated using rotary handle Free standing, floor mounting Switchboard fabricated out of 16SWG CRCA sheet with Bottom Cable entry at incomer & Top cable exit at outgoing side. | [53 empty] | 27 | Supplying, fabrication, installation,testing and commissioing of cubicle type prewired LT Panel suitable for 415 Volt, 3 phase, 4 wire 50 HZ AC supply system, floor mounted, fabricated in compartmentalized design from CRCA steel of 1.6 mm thick for frame work and covers, 3 mm thick for gland plates, including finishing with powder coated, dust and vermin proof complete with 7 tank process having extensible type aluminium bus bar with full rated neutral of high conductivity ,3 mm FRP / SMC Sheet for shrouding, base frame of M.S. channel section of not less than 75 mm x 40 mmx6mm thick, copper earth bar of size 25mmx 5mm or at the rear with 2 No. earth stud, complete with 1.5sqmm FRLS PVC insulated copper conducter for control wires, cable alleys, cable gland plates, including following : All MCCB shall have ICu =100% ICs MCCB shall be operated using rotary handle Free standing, floor mounting Switchboard fabricated out of 16SWG CRCA sheet with Bottom Cable entry at incomer & Top cable exit at outgoing side.
27.1 | Main Panel: Incomer: 400A,36kA,4 pole, Moulded Case Circuit Breaker with Thermal magentic,earth fault and shunt release-1no. Out going: 250A,36KA, 4 pole Moulded Case Circuit Breaker with Thermal magnetic release – 2nos. 160A,36KA, 4 pole Moulded Case Circuit Breaker with Thermal magnetic release – 2nos. Bus bar: 4 Strip aluminium bus bar of 400 A, 415 V capacity with full rate neutral, heat shrinkable coloured sleeves complete for withstanding 35 KA fault - 1 set Metering and indications: Multifunction meter Class 1.0 for measuring voltage, current, power factor, frequency, THD, power, kWH,kVA,kVAR, kVARh, with RS485 port -1 no. Current Transformer- Cast resin 400/5A with class- 1 accuracy and 15 VA burden - 3nos. RYB phase indicating LEDs-3nos. Trip, ON, OFF indicating LEDs-3nos. 2A control SPMCBs-4nos. Surge Suppresser of type2 3P+N 40kA -1no. |  | 1 | Each | 187281 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 27.1 | Main Panel: Incomer: 400A,36kA,4 pole, Moulded Case Circuit Breaker with Thermal magentic,earth fault and shunt release-1no. Out going: 250A,36KA, 4 pole Moulded Case Circuit Breaker with Thermal magnetic release – 2nos. 160A,36KA, 4 pole Moulded Case Circuit Breaker with Thermal magnetic release – 2nos. Bus bar: 4 Strip aluminium bus bar of 400 A, 415 V capacity with full rate neutral, heat shrinkable coloured sleeves complete for withstanding 35 KA fault - 1 set Metering and indications: Multifunction meter Class 1.0 for measuring voltage, current, power factor, frequency, THD, power, kWH,kVA,kVAR, kVARh, with RS485 port -1 no. Current Transformer- Cast resin 400/5A with class- 1 accuracy and 15 VA burden - 3nos. RYB phase indicating LEDs-3nos. Trip, ON, OFF indicating LEDs-3nos. 2A control SPMCBs-4nos. Surge Suppresser of type2 3P+N 40kA -1no. | 1 | Each
27.2 | UPS Panel: Incomer: 250A,36kA,4 pole, Moulded Case Circuit Breaker with Thermal magentic release-1no. Out going: 125A,25KA, 4 pole Moulded Case Circuit Breaker with Thermal magnetic release – 3nos. Bus bar: 4 Strip aluminium bus bar of 250 A, 415 V capacity with full rate neutral, heat shrinkable coloured sleeves complete for withstanding 35 KA fault - 1 set Metering and indications: Multifunction meter Class 1.0 for measuring voltage, current, power factor, frequency, THD, power, kWH,kVA,kVAR,kVARh, with RS485 port -1 no. Current Transformer- Cast resin 250/5A with class- 1 accuracy and 15 VA burden - 3nos. RYB phase indicating LEDs-3nos. Trip, ON, OFF indicating LEDs-3nos. 2A control SPMCBs-4nos. |  | 1 | Each | 101309 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 27.2 | UPS Panel: Incomer: 250A,36kA,4 pole, Moulded Case Circuit Breaker with Thermal magentic release-1no. Out going: 125A,25KA, 4 pole Moulded Case Circuit Breaker with Thermal magnetic release – 3nos. Bus bar: 4 Strip aluminium bus bar of 250 A, 415 V capacity with full rate neutral, heat shrinkable coloured sleeves complete for withstanding 35 KA fault - 1 set Metering and indications: Multifunction meter Class 1.0 for measuring voltage, current, power factor, frequency, THD, power, kWH,kVA,kVAR,kVARh, with RS485 port -1 no. Current Transformer- Cast resin 250/5A with class- 1 accuracy and 15 VA burden - 3nos. RYB phase indicating LEDs-3nos. Trip, ON, OFF indicating LEDs-3nos. 2A control SPMCBs-4nos. | 1 | Each
27.3 | Supply and installation of 250A, 4pole, MCCB isolator on Wall mounted Enclosure fabricated out of 16SWG CRCA sheet with Top/bottom Cable entry suitable for terminating 1Rx4Cx 150Sq.mm al Ar. Cable on top and bottom cable exit suitable for termination of 4Rx1Cx70Sq.mm Cu flexible cable. |  | 1 | Each | 24240 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 27.3 | Supply and installation of 250A, 4pole, MCCB isolator on Wall mounted Enclosure fabricated out of 16SWG CRCA sheet with Top/bottom Cable entry suitable for terminating 1Rx4Cx 150Sq.mm al Ar. Cable on top and bottom cable exit suitable for termination of 4Rx1Cx70Sq.mm Cu flexible cable. | 1 | Each
28 | Supply and laying UTP 4pair CAT 6 LAN cable in the existing surface/recessed PVC conduit as required. | [53 empty] | 28 | Supply and laying UTP 4pair CAT 6 LAN cable in the existing surface/recessed PVC conduit as required.
28.1 | 1 run of cable |  | 1318 | metre | 57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 28.1 | 1 run of cable | 1318 | metre
29 | Supplying & fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | [53 empty] | 29 | Supplying & fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
29.1 | 25mm |  | 603 | metre | 57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 29.1 | 25mm | 603 | metre
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information