## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Electrical works for new lab at Room no. 1203, Physical Science Block in IISER, Thiruvananthpuram
Contact No: 0471-2778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Basic unit Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required. | [53 empty] | 1 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required.
1.1 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire |  | 355 | metre | 355.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.1 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire | 355 | metre
1.2 | 4 x 4 sq.mm + 2 x 4 sq.mm earth wire |  | 88 | metre | 571 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.2 | 4 x 4 sq.mm + 2 x 4 sq.mm earth wire | 88 | metre
1.3 | 4 x 10 sq.mm + 2 x 6 sq.mm earth wire (For Raw power DB) |  | 40 | metre | 1068.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.3 | 4 x 10 sq.mm + 2 x 6 sq.mm earth wire (For Raw power DB) | 40 | metre
2 | Supply & fixing of following size of three compartments Dado trunking for distribution of power, data & telecommunication cables made up of UPVC material shall be non-corrosive and excellent resistance to minerals, acid, alkalies and detergent. The three compartment system shall have cross sectional dimensions of 170mm height and 57mm in depth and with a wall thickness of 1.7mm on lid and 2mm on cover. The main carrier should be pre-drilled at 300mm centers with a divider knockout after every 100mm intervals. Material should be non flame prorogating and a Class 1 spread of flame achieved when tested in accordance with the requirements of BS EN 50085-1:1999 and BS EN 61386-1:2004 | [53 empty] | 2 | Supply & fixing of following size of three compartments Dado trunking for distribution of power, data & telecommunication cables made up of UPVC material shall be non-corrosive and excellent resistance to minerals, acid, alkalies and detergent. The three compartment system shall have cross sectional dimensions of 170mm height and 57mm in depth and with a wall thickness of 1.7mm on lid and 2mm on cover. The main carrier should be pre-drilled at 300mm centers with a divider knockout after every 100mm intervals. Material should be non flame prorogating and a Class 1 spread of flame achieved when tested in accordance with the requirements of BS EN 50085-1:1999 and BS EN 61386-1:2004
2.1 | Main carrier 170mm (H) x 57mm(D) complete with Straight & Curved cover along with accessories such as internal and external corner, Flat Tee, cable retainer, joint cover, end cap etc as required. |  | 48 | metre | 2275.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.1 | Main carrier 170mm (H) x 57mm(D) complete with Straight & Curved cover along with accessories such as internal and external corner, Flat Tee, cable retainer, joint cover, end cap etc as required. | 48 | metre
3 | Supplying and fixing following modular cover/base plate and box in the existing PVC wall trunking as mentioned in item no.2.0 including connections etc. as required. | [53 empty] | 3 | Supplying and fixing following modular cover/base plate and box in the existing PVC wall trunking as mentioned in item no.2.0 including connections etc. as required.
3.1 | 4 Module (White) with blank plate |  | 5 | Each | 514.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.1 | 4 Module (White) with blank plate | 5 | Each
3.2 | 6 Module (White) |  | 8 | Each | 590.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.2 | 6 Module (White) | 8 | Each
3.3 | 4 Module (Black) with blank plate |  | 4 | Each | 585.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.3 | 4 Module (Black) with blank plate | 4 | Each
3.4 | 6 Module (Black) |  | 32 | Each | 727.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.4 | 6 Module (Black) | 32 | Each
4 | Supplying and fixing following modular switches and sockets in the existing PVC wall trunking as mentioned in item no.2.0 including connections etc. as required. | [53 empty] | 4 | Supplying and fixing following modular switches and sockets in the existing PVC wall trunking as mentioned in item no.2.0 including connections etc. as required.
4.1 | 15/16A switch (Black) |  | 65 | Each | 245.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.1 | 15/16A switch (Black) | 65 | Each
4.2 | 6 pin 15/16A socket (Black) |  | 65 | Each | 337.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.2 | 6 pin 15/16A socket (Black) | 65 | Each
4.3 | 15/16A switch (white) |  | 20 | Each | 165.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.3 | 15/16A switch (white) | 20 | Each
4.4 | 6 pin 15/16A socket (white) |  | 20 | Each | 209.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.4 | 6 pin 15/16A socket (white) | 20 | Each
5 | Fixing of 4/8/12 ways surface mounted vertical type 415V TPN MCB distribution board of sheet steel, dust protected duly powder painted inclusive of tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCbs (but without MCBs and incomer) as required. Note: (Legrand make Vertical DB shall be supplied by The Department at free of cost. |  | 1 | Each | 486.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5 | Fixing of 4/8/12 ways surface mounted vertical type 415V TPN MCB distribution board of sheet steel, dust protected duly powder painted inclusive of tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCbs (but without MCBs and incomer) as required. Note: (Legrand make Vertical DB shall be supplied by The Department at free of cost. | 1 | Each
6 | Supplying and fixing 5A to 32A rating, 240/415V, 10kA, "C" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand/Siemens | [53 empty] | 6 | Supplying and fixing 5A to 32A rating, 240/415V, 10kA, "C" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand/Siemens
6.1 | Single pole |  | 26 | Each | 272.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.1 | Single pole | 26 | Each
6.2 | Triple pole |  | 5 | Each | 1070.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.2 | Triple pole | 5 | Each
7 | Supplying and fixing following rating four pole 415V residual current circuit breaker (RCCB), having a sensitivity current of 100mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand | [53 empty] | 7 | Supplying and fixing following rating four pole 415V residual current circuit breaker (RCCB), having a sensitivity current of 100mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand
7.1 | 40A 4P RCCB (for PDB) |  | 1 | Each | 3232.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7.1 | 40A 4P RCCB (for PDB) | 1 | Each
8 | Supplying and fixing following rating four pole 415V miniature circuit breaker (MCB) 'C' curve, in the existing MCB DB/panel complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand | [53 empty] | 8 | Supplying and fixing following rating four pole 415V miniature circuit breaker (MCB) 'C' curve, in the existing MCB DB/panel complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand
8.1 | 40A 4P MCB (for PDB) |  | 1 | Each | 2009.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 8.1 | 40A 4P MCB (for PDB) | 1 | Each
9 | Supply, Installation, testing and commissioning of 25A 4P 30mA RCCB with added immunity and 20amps C curve Four pole MCB, on industrial Power Plug Sockets in sheet steel enclosure, on surface and complete with interconnections as required. (Industrial power socket enclosure with plug top will be issued by department) |  | 5 | Each | 6521 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 9 | Supply, Installation, testing and commissioning of 25A 4P 30mA RCCB with added immunity and 20amps C curve Four pole MCB, on industrial Power Plug Sockets in sheet steel enclosure, on surface and complete with interconnections as required. (Industrial power socket enclosure with plug top will be issued by department) | 5 | Each
10 | Supply, Installation, Testing and Commissioning on Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn |  | 2 | Each | 11170.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 10 | Supply, Installation, Testing and Commissioning on Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn | 2 | Each
11 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit as required |  | 25 | mtr | 135 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 11 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit as required | 25 | mtr
12 | Supplying and fixing of 20mm medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required |  | 10 | mtr | 136.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 12 | Supplying and fixing of 20mm medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required | 10 | mtr
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information