## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Dedicated earth station for instruments in Common Instrumentation Lab at CSB, IISER, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply, Installation, Testing and Commissioning on Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn |  | 3 | Each | 10505.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply, installation, testing and commissioning of pre-wired LED street light with lumen level not less than 3000lumens and not more than 30W power, the fixture should be epoxy powder coated pressure diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 5700K pure white, min 4KV surge protection, IP66 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required. (Approved makes: Bajaj Cat No: ENXT P 36L WH PO PC SD/ Wipro : LR02-331-XXX-55XX, Havells: ENDURA CITYLITEPLATPLUSSL30WLED) | 8 | Each
2 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit as required |  | 110 | Mtr | 127 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Fabrication, supply, and fixing of street light pole made of 80mm dia, 4.5 mtr high, class 'C' GI pipe with 300mmx300mm x16mm MS plate welded to the base along with top arm bracket length 3 feet suitable for mounting LED street light fixtures as mentioned in item no. 1.0, cutting, threading, welding, earth excavation, providing PCC pedestal as per site requirement, coping, including supply of GI pipe, weather proof terminal box of suitable size with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, 50mm dia GI sleeve for cable entry, earthing etc complete as required and painting with two coats of epoxy primer and epoxy paint complete as required and as directed by Engineer in charge. (Drawing of the pole shall be got approved from EIC prior to fabrication) (Weather proof terminal box: Sintex Model No. GSJB-2014/Equivalent) | 8 | Each
3 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required |  | 90 | Mtr | 128 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3.1 | 3C x 4 sqmm Aluminium armoured cable | 100 | Metre
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information