## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Minor Electrical works in Labs CSB 3206, CSB1102(CIL), PSB 1201B, PSB 1202A, LHC and Residence blocks at IISER, Thiruvananthpuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required. | [53 empty] | 1 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required.
1.1 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire |  | 140 | metre | 355.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.1 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire | 140 | metre
1.2 | 4 x 4 sq.mm + 2 x 4 sq.mm earth wire |  | 28 | metre | 571 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.2 | 4 x 4 sq.mm + 2 x 4 sq.mm earth wire | 28 | metre
1.3 | 2 x 6 sq.mm + 1 x 6 sq.mm earth wire |  | 20 | metre | 466.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.3 | 2 x 6 sq.mm + 1 x 6 sq.mm earth wire | 20 | metre
2 | Supplying and fixing following modular switch/ socket with modular plate & switch box including connections as required | [53 empty] | 2 | Supplying and fixing following modular switch/ socket with modular plate & switch box including connections as required
2.1 | 5/6 amps switch |  | 4 | Each | 109.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.1 | 5/6 amps switch | 4 | Each
2.2 | 15/16 A switch |  | 14 | Each | 165.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.2 | 15/16 A switch | 14 | Each
2.3 | 3 pin 5/6 A socket outlet |  | 4 | Each | 129.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.3 | 3 pin 5/6 A socket outlet | 4 | Each
2.4 | 6 pin 15/16 A socket outlet |  | 14 | Each | 209.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.4 | 6 pin 15/16 A socket outlet | 14 | Each
2.5 | 6 Module Modular base & cover plate |  | 9 | Each | 193.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.5 | 6 Module Modular base & cover plate | 9 | Each
2.6 | 6 Module PVC surface box |  | 2 | Each | 320.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.6 | 6 Module PVC surface box | 2 | Each
2.7 | 6 Module mounting box suitable for existing Honey well Prestige 3D Cable management system |  | 7 | Each | 458.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.7 | 6 Module mounting box suitable for existing Honey well Prestige 3D Cable management system | 7 | Each
3 | Fixing of of 8/12Way single pole and neutral. Sheet steel, MCB distribution board, 240V, on surface, complete with tinned copper bus bar, neutral nus bar, earth bar, din bar, interconnections, powder painted including earthing etc as required but without MCB/RCCB/Isolator Note: (Legrand make DB shall be supplied by The Department at free of cost. |  | 1 | Each | 315.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Fixing of of 8/12Way single pole and neutral. Sheet steel, MCB distribution board, 240V, on surface, complete with tinned copper bus bar, neutral nus bar, earth bar, din bar, interconnections, powder painted including earthing etc as required but without MCB/RCCB/Isolator Note: (Legrand make DB shall be supplied by The Department at free of cost. | 1 | Each
4 | Supplying and fixing 5A to 32A rating, 240/415V, 10kA, "C" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand | [53 empty] | 4 | Supplying and fixing 5A to 32A rating, 240/415V, 10kA, "C" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand
4.1 | Single pole |  | 6 | Each | 272.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | Single pole | 6 | Each
4.2 | Double pole |  | 2 | Each | 697.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.2 | Double pole | 2 | Each
5 | Supplying and fixing following rating double pole 240V residual current circuit breaker (RCCB), having a sensitivity current of 30mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand | [53 empty] | 5 | Supplying and fixing following rating double pole 240V residual current circuit breaker (RCCB), having a sensitivity current of 30mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand
5.1 | 32/40A |  | 1 | Each | 2809.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.1 | 32/40A | 1 | Each
5.2 | 25A |  | 1 | Each | 2156.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.2 | 25A | 1 | Each
6 | Supplying and fixing DP steel enclosure on surface along with 32A 240V 'C' curve MCB complete with connections, testing and commissioning etc as required. |  | 1 | Each | 1243 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6 | Supplying and fixing DP steel enclosure on surface along with 32A 240V 'C' curve MCB complete with connections, testing and commissioning etc as required. | 1 | Each
7 | Supplying and fixing DP steel enclosure on surface along with 25A DP 30mA RCCB complete with connections, testing and commissioning etc as required. |  | 1 | Each | 2681.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7 | Supplying and fixing DP steel enclosure on surface along with 25A DP 30mA RCCB complete with connections, testing and commissioning etc as required. | 1 | Each
8 | Supplying and fixing FP steel enclosure on surface along with 25A 4P 30mA RCCB complete with connections, testing and commissioning etc as required. |  | 1 | Each | 3289.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 8 | Supplying and fixing FP steel enclosure on surface along with 25A 4P 30mA RCCB complete with connections, testing and commissioning etc as required. | 1 | Each
9 | Supply, Installation, Testing and Commissioning on Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn |  | 1 | Each | 11170.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 9 | Supply, Installation, Testing and Commissioning on Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn | 1 | Each
10 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit as required |  | 35 | mtr | 135 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10 | Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit as required | 35 | mtr
11 | Supplying and fixing of 20mm medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required |  | 26 | mtr | 136.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 11 | Supplying and fixing of 20mm medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required | 26 | mtr
12 | Supplying and fixing of following sizes of UPVC Cable Management System/Mini Trunking System along with accessories on surface including supply of fixing materials, interconnecting clamps,bends,end caps, joint covers, internal and external corners, dividers, fixing screws as required | [53 empty] | 12 | Supplying and fixing of following sizes of UPVC Cable Management System/Mini Trunking System along with accessories on surface including supply of fixing materials, interconnecting clamps,bends,end caps, joint covers, internal and external corners, dividers, fixing screws as required
12.1 | 25mm x 12mm |  | 8 | metre | 85.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 12.1 | 25mm x 12mm | 8 | metre
13 | Supply of following size 1.1kV,PVC FRLS sheathed XLPE insulated copper cable. | [53 empty] | 13 | Supply of following size 1.1kV,PVC FRLS sheathed XLPE insulated copper cable.
13.1 | 1C x 120sqmm XLPE insulated copper armoured cable. |  | 16 | metre | 2753.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 13.1 | 1C x 120sqmm XLPE insulated copper armoured cable. | 16 | metre
13.2 | 1C x 35sqmm XLPE insulated copper armoured cable. |  | 75 | metre | 829.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 13.2 | 1C x 35sqmm XLPE insulated copper armoured cable. | 75 | metre
13.3 | 4C x 16sqmm XLPE insulated copper unarmoured cable. |  | 20 | metre | 1175.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 13.3 | 4C x 16sqmm XLPE insulated copper unarmoured cable. | 20 | metre
14 | Laying and fixing of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1kV grade of following size on cable tray as required. | [53 empty] | 14 | Laying and fixing of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1kV grade of following size on cable tray as required.
14.1 | Upto 35sq.mm (clamped with 1mm thick saddle) |  | 95 | metre | 47.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 14.1 | Upto 35sq.mm (clamped with 1mm thick saddle) | 95 | metre
14.2 | Above 95sq.mm and upto 185sq.mm (clamped with 1mm thick saddle) |  | 16 | metre | 122.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 14.2 | Above 95sq.mm and upto 185sq.mm (clamped with 1mm thick saddle) | 16 | metre
15 | Supplying and making end termination with gland and lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1kV grade as required. | [53 empty] | 15 | Supplying and making end termination with gland and lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1kV grade as required.
15.1 | 1C x 120sqmm XLPE insulated copper armoured cable. |  | 2 | each | 652 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 15.1 | 1C x 120sqmm XLPE insulated copper armoured cable. | 2 | each
15.2 | 1C x 35sqmm XLPE insulated copper armoured cable. |  | 4 | each | 199.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 15.2 | 1C x 35sqmm XLPE insulated copper armoured cable. | 4 | each
15.3 | 4C x 16sqmm XLPE insulated copper unarmoured cable. |  | 2 | each | 221.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 15.3 | 4C x 16sqmm XLPE insulated copper unarmoured cable. | 2 | each
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information