## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer, IISER Thiruvananthapuram
Name of Work: Supply and installation of LED flood lighting for the Football ground at IISER, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply and installation of 16Mtr height Stadium Mast of follwing specification suitable for mounting upto 24 nos. of 500/1000 Watt LED Flood Light Fixtures and all materials required for installation like foundation bolts, RCC pole foundation as per the pole manufacturer recommended drawing, connections complete as required and all related works as directed by the Engineer in charge. Main mast Height: 14 m Head Frame shaft Height (Vertical): 2 m Main mast Sections: 2 Mast and Head frame material: Hot Dipped Galvanized Iron Top Diameter: 150 mm minimum Bottom Diameter: 410 mm minimum Thickness:4mm Size of base plate: 540mm minimum BAse plate thickness: 20mm minimum No. of foundation bolt: 8 minimum Wind Speed: Not less than 39m/s Safety cage ladder: required Maintenance platform on the head frame: required (Pole-Bajaj/Crompton/Trasnrail/Klite) Note: GAD of pole and pole foundation should be get approved from the Engineer in charge prior to execution. |  | 4 | Each | 503797 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply and installation of 16Mtr height Stadium Mast of follwing specification suitable for mounting upto 24 nos. of 500/1000 Watt LED Flood Light Fixtures and all materials required for installation like foundation bolts, RCC pole foundation as per the pole manufacturer recommended drawing, connections complete as required and all related works as directed by the Engineer in charge. Main mast Height: 14 m Head Frame shaft Height (Vertical): 2 m Main mast Sections: 2 Mast and Head frame material: Hot Dipped Galvanized Iron Top Diameter: 150 mm minimum Bottom Diameter: 410 mm minimum Thickness:4mm Size of base plate: 540mm minimum BAse plate thickness: 20mm minimum No. of foundation bolt: 8 minimum Wind Speed: Not less than 39m/s Safety cage ladder: required Maintenance platform on the head frame: required (Pole-Bajaj/Crompton/Trasnrail/Klite) Note: GAD of pole and pole foundation should be get approved from the Engineer in charge prior to execution. | 4 | Each
2 | Supply, installation, testing and commssioning of following type high performance LED flood light luminaire of max 500W, 5700K,min 60000lumen with lumen efficiency of 120 lm/W with pressure die cast housing, toughned glass and individual LEDs with seconary lens optics along with IP66 protection, 4kV internal and 10kV external surge protection on the stadium mast as mentioned in item no.1.0 using necessary supports and interconnections as required. (Make: Philips/Bajaj/Crompton/Havells/Osram) | [53 empty] | 2 | Supply, installation, testing and commssioning of following type high performance LED flood light luminaire of max 500W, 5700K,min 60000lumen with lumen efficiency of 120 lm/W with pressure die cast housing, toughned glass and individual LEDs with seconary lens optics along with IP66 protection, 4kV internal and 10kV external surge protection on the stadium mast as mentioned in item no.1.0 using necessary supports and interconnections as required. (Make: Philips/Bajaj/Crompton/Havells/Osram)
2.1 | Luminaire with 30 degree beam angle |  | 40 | Each | 33931 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.1 | Luminaire with 30 degree beam angle | 40 | Each
2.2 | Luminaire with 60 degree beam angle |  | 16 | Each | 33649 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.2 | Luminaire with 60 degree beam angle | 16 | Each
3 | Supply, installation testing and commissioning of weather proof Thermoplastic circuit breaker box - 2row 24modules of IP 65 protection, IK09 with clear acrylic front door, metric knockouts for cable entry and fixing the box on floor using necessary angle iron frame complete as required and as directed by Engineer in charge on Make : Legrand/Henzel |  | 4 | Each | 6073 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supply, installation testing and commissioning of weather proof Thermoplastic circuit breaker box - 2row 24modules of IP 65 protection, IK09 with clear acrylic front door, metric knockouts for cable entry and fixing the box on floor using necessary angle iron frame complete as required and as directed by Engineer in charge on Make : Legrand/Henzel | 4 | Each
4 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required (Make: Legrand DX3/Schneider-ACT19/Siemens-3WL/L&T) | [53 empty] | 4 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required (Make: Legrand DX3/Schneider-ACT19/Siemens-3WL/L&T)
4.1 | Double pole |  | 12 | Each | 945.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | Double pole | 12 | Each
4.2 | Triple pole and neutral pole |  | 4 | Each | 1770.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.2 | Triple pole and neutral pole | 4 | Each
5 | Supplying and fixing following rating four pole(three phase and neutral),415V, Residual Current Circuit Breaker(RCCB) having a sensitve current of 30mA, in the existing MCB DB complete with connections, testing and commissioning etc. as required (Make: Legrand DX3/Schneider-ACT19/Siemens-3WL/L&T) | [53 empty] | 5 | Supplying and fixing following rating four pole(three phase and neutral),415V, Residual Current Circuit Breaker(RCCB) having a sensitve current of 30mA, in the existing MCB DB complete with connections, testing and commissioning etc. as required (Make: Legrand DX3/Schneider-ACT19/Siemens-3WL/L&T)
5.1 | 32A |  | 4 | Each | 3727.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.1 | 32A | 4 | Each
6 | Lighting Control Panel Fabrication,supply, installation, testing and commissioning of 415V, 3-phase, 50 Hz, totally enclosed, free standing, dust, damp, vermin proof, hinged, lockable, double door on both side with 70 cm long legs, out door type Feeder Pillar with IP:65 protection made out of 2 mm thick MS sheet complete with Bus Bars, M.V. danger notice plate, multi funciton meter , indicating lamps, with suitable capacity solid aluminium strips, connections of incoming and outgoing cables by thimble, base frame of 50x50x6 MS angle iron with canopy on top, complete as required and having following incoming and outgoing feeders separately housed in 16 SWG sheet steel enclosure contactors, MCCB/MCB complete as per specifications and including PCC foundation, plastering etc. complete as required. MCCB shall have ICU =100% ICS MCCB should be thermal magnetic, with shunt and Trip alarm contacts (Make: Legrand DX3/Schneider-ACT19/Siemens-3WL/L&T) | [53 empty] | 6 | Lighting Control Panel Fabrication,supply, installation, testing and commissioning of 415V, 3-phase, 50 Hz, totally enclosed, free standing, dust, damp, vermin proof, hinged, lockable, double door on both side with 70 cm long legs, out door type Feeder Pillar with IP:65 protection made out of 2 mm thick MS sheet complete with Bus Bars, M.V. danger notice plate, multi funciton meter , indicating lamps, with suitable capacity solid aluminium strips, connections of incoming and outgoing cables by thimble, base frame of 50x50x6 MS angle iron with canopy on top, complete as required and having following incoming and outgoing feeders separately housed in 16 SWG sheet steel enclosure contactors, MCCB/MCB complete as per specifications and including PCC foundation, plastering etc. complete as required. MCCB shall have ICU =100% ICS MCCB should be thermal magnetic, with shunt and Trip alarm contacts (Make: Legrand DX3/Schneider-ACT19/Siemens-3WL/L&T)
6.1 | Incomer: 100A, TPN, MCCB of 36kA -1no. Busbar: 4 Strip aluminium bus bar of 100 A, 415 V capacity with full rate neutral, heat shrinkable coloured sleeves complete for withstanding 35 KA fault - 1 set Outgoing: 40A. 4pole MCCB, 25kA with Thermal magentic release-4nos. 40A, 3 pole contactor with 1NO-1NC-4nos. 25A,4pole, MCB-1no. 25A, 3 pole contactor with 1NO-1NC-1no. Surge supressor for protection against direct and indirect lightning surges-1no. Metering and indications: Multifunction meter Class 1.0 for measuring voltage, current, power factor, frequency, THD, power, kWH,kVA,kVAR,kVARh, with RS485 port -1 no. Current Transformer- Cast resin 100/5A with class- 1 accuracy and 15 VA burden - 3nos. RYB phase indicating LEDs-3nos. Trip, ON, OFF indicating LEDs-3nos. 2A control SPMCBs-4nos. Controls: ON push button with LED indication(Red)-5 nos. OFF push button with LED indication(Green)-5 nos. |  | 1 | Each | 114904.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6.1 | Incomer: 100A, TPN, MCCB of 36kA -1no. Busbar: 4 Strip aluminium bus bar of 100 A, 415 V capacity with full rate neutral, heat shrinkable coloured sleeves complete for withstanding 35 KA fault - 1 set Outgoing: 40A. 4pole MCCB, 25kA with Thermal magentic release-4nos. 40A, 3 pole contactor with 1NO-1NC-4nos. 25A,4pole, MCB-1no. 25A, 3 pole contactor with 1NO-1NC-1no. Surge supressor for protection against direct and indirect lightning surges-1no. Metering and indications: Multifunction meter Class 1.0 for measuring voltage, current, power factor, frequency, THD, power, kWH,kVA,kVAR,kVARh, with RS485 port -1 no. Current Transformer- Cast resin 100/5A with class- 1 accuracy and 15 VA burden - 3nos. RYB phase indicating LEDs-3nos. Trip, ON, OFF indicating LEDs-3nos. 2A control SPMCBs-4nos. Controls: ON push button with LED indication(Red)-5 nos. OFF push button with LED indication(Green)-5 nos. | 1 | Each
7 | Supply of FRLS XLPE power cable of 1.1 kV grade of following size as required. (Make: Universal/Polycab/Gloster/RRKabel/Havells) | [53 empty] | 7 | Supply of FRLS XLPE power cable of 1.1 kV grade of following size as required. (Make: Universal/Polycab/Gloster/RRKabel/Havells)
7.1 | 3C x 4 sqmm Copper armoured cable |  | 85 | Metre | 238 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.1 | 3C x 4 sqmm Copper armoured cable | 85 | Metre
7.2 | 4C x 25sqmm Aluminium armoured cable |  | 100 | Metre | 246 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.2 | 4C x 25sqmm Aluminium armoured cable | 100 | Metre
7.3 | 4C x 35sqmm Aluminium armoured cable |  | 450 | Metre | 331 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.3 | 4C x 35sqmm Aluminium armoured cable | 450 | Metre
7.4 | 3.5C x 70sqmm Aluminium armoured cable |  | 200 | Metre | 529 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.4 | 3.5C x 70sqmm Aluminium armoured cable | 200 | Metre
7.5 | 4C x 6sqmm Aluminium armoured cable |  | 500 | Metre | 133 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7.5 | 4C x 6sqmm Aluminium armoured cable | 500 | Metre
8 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | [53 empty] | 8 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
8.1 | 63 mm dia (OD-63 mm & ID-50 mm nominal) |  | 200 | Metre | 356 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 8.1 | 63 mm dia (OD-63 mm & ID-50 mm nominal) | 200 | Metre
8.2 | 50 mm dia (OD-50 mm & ID-38 mm nominal) |  | 950 | Metre | 143 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 8.2 | 50 mm dia (OD-50 mm & ID-38 mm nominal) | 950 | Metre
9 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC HUME/ METAL/DWC HDPE pipe as required. | [53 empty] | 9 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC HUME/ METAL/DWC HDPE pipe as required.
9.1 | Upto 35 sq. mm |  | 1050 | Metre | 53 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 9.1 | Upto 35 sq. mm | 1050 | Metre
9.2 | above 35smm upto 95sqmm |  | 200 | Metre | 82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 9.2 | above 35smm upto 95sqmm | 200 | Metre
10 | Supplying and making end termination with brass compression gland for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1kV grade as required. | [53 empty] | 10 | Supplying and making end termination with brass compression gland for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1kV grade as required.
10.1 | 3C x 4 sqmm Copper armoured cable |  | 112 | Each | 373 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10.1 | 3C x 4 sqmm Copper armoured cable | 112 | Each
10.2 | 4 core x 25sqmm (28mm) |  | 4 | Each | 454 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10.2 | 4 core x 25sqmm (28mm) | 4 | Each
10.3 | 4 core x 35sqmm (32mm) |  | 4 | Each | 533 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10.3 | 4 core x 35sqmm (32mm) | 4 | Each
10.4 | 3.5core x 70sqmm(38mm) |  | 2 | Each | 675 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10.4 | 3.5core x 70sqmm(38mm) | 2 | Each
10.5 | 4C x 6sqmm Aluminium armoured cable |  | 12 | Each | 388 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10.5 | 4C x 6sqmm Aluminium armoured cable | 12 | Each
11 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/coke and salt as required. (For lightning protection and protective earthing.) |  | 10 | Each | 10772 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 11 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/coke and salt as required. (For lightning protection and protective earthing.) | 10 | Each
12 | Supplying and laying 20 mm X 3 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) |  | 50 | meter | 129 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 12 | Supplying and laying 20 mm X 3 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 50 | meter
13 | Erection of metallic flood light pole of height 9.0 metre in reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required Note: Flood light pole along with mounting bracket will be issued by Department |  | 2 | Each | 12593 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 13 | Erection of metallic flood light pole of height 9.0 metre in reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling etc. as required Note: Flood light pole along with mounting bracket will be issued by Department | 2 | Each
14 | Supply, installation, testing and commssioning of high performance LED flood light luminaire of max 50W, 5700K,min 6000lumen with lumen efficiency of 120 lm/W with pressure die cast housing, toughned glass and individual LEDs with secondary lens optics along with IP66 protection, 10kV internal surge protection on the poles as mentioned in item no.15.0 using necessary supports and interconnections as required. (Make: Philips/Bajaj/Crompton/Havells/Osram) |  | 14 | Each | 3600 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 14 | Supply, installation, testing and commssioning of high performance LED flood light luminaire of max 50W, 5700K,min 6000lumen with lumen efficiency of 120 lm/W with pressure die cast housing, toughned glass and individual LEDs with secondary lens optics along with IP66 protection, 10kV internal surge protection on the poles as mentioned in item no.15.0 using necessary supports and interconnections as required. (Make: Philips/Bajaj/Crompton/Havells/Osram) | 14 | Each
15 | Supply and installation of weather proof terminal boxes of IP 66 protection, IK09 with cable connecting terminals, metric knockouts for cable entry and fixing the box on the head frame of light mast complete as required and as directed by Engineer in charge on Make : Legrand/Henzel or equivalent |  | 60 | Each | 850 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 15 | Supply and installation of weather proof terminal boxes of IP 66 protection, IK09 with cable connecting terminals, metric knockouts for cable entry and fixing the box on the head frame of light mast complete as required and as directed by Engineer in charge on Make : Legrand/Henzel or equivalent | 60 | Each
16 | Supplying and embedding following dia G.I. pipe (medium class) in pole collar/ foundation (during casting) for cable entry including bending the pipe to the required shape complete as required. | [53 empty] | 16 | Supplying and embedding following dia G.I. pipe (medium class) in pole collar/ foundation (during casting) for cable entry including bending the pipe to the required shape complete as required.
16.1 | 40mm |  | 36 | mtr | 849.1 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 16.1 | 40mm | 36 | mtr
17 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. |  | 4 | each | 746.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 17 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 4 | each
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information