## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Electrical works for Lab no. B202, Biological Science Block in IISER, Thiruvananthpuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required. | [53 empty] | 1 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recessed medium class PVC conduit as required.
1.1 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire |  | 63 | metre | 355.14 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.1 | 2 x 4 sq.mm + 1 x 4 sq.mm earth wire | 63 | metre
1.2 | 4 x 6 sq.mm + 2 x 6 sq.mm earth wire |  | 20 | metre | 801.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.2 | 4 x 6 sq.mm + 2 x 6 sq.mm earth wire | 20 | metre
2 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor single core cable in the existing surface/recesed PVC conduit/CMS etc as required. | [53 empty] | 2 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor single core cable in the existing surface/recesed PVC conduit/CMS etc as required.
2.1 | 3 x 4 sq.mm |  | 150 | metre | 219.04 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.1 | 3 x 4 sq.mm | 150 | metre
2.2 | 6 x 6 sq.mm |  | 19 | metre | 635.85 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2.2 | 6 x 6 sq.mm | 19 | metre
3 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor single core cable through uPVC mini trunking of size 25x12mm as required. | [53 empty] | 3 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor single core cable through uPVC mini trunking of size 25x12mm as required.
3.1 | 3 x 4 sq.mm |  | 10 | metre | 301.5 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3.1 | 3 x 4 sq.mm | 10 | metre
4 | Supplying and fixing of following sizes of uPVC Cable Management System System along with accessories on surface including supply of fixing materials, internal couplers, joint covers, end caps, internal and external corners, dividers, cable retainers, angles tee etc fixing screws as required and connected to the existing CMS system (MK - Prestige 3D). | [53 empty] | 4 | Supplying and fixing of following sizes of uPVC Cable Management System System along with accessories on surface including supply of fixing materials, internal couplers, joint covers, end caps, internal and external corners, dividers, cable retainers, angles tee etc fixing screws as required and connected to the existing CMS system (MK - Prestige 3D).
4.1 | 170mm x 50mm |  | 30 | metre | 1550.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4.1 | 170mm x 50mm | 30 | metre
5 | Dismantling and refixing of the existing 170mm x 50mm size UPVC Cable management system on wall completed as required with necessary fixing accessories. |  | 12 | metre | 86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5 | Dismantling and refixing of the existing 170mm x 50mm size UPVC Cable management system on wall completed as required with necessary fixing accessories. | 12 | metre
6 | Supplying and fixing following size/modules, PVC box suitable for item No.4 alongwith modular base & cover plate for modular switches in existing Cable management system etc as required. | [53 empty] | 6 | Supplying and fixing following size/modules, PVC box suitable for item No.4 alongwith modular base & cover plate for modular switches in existing Cable management system etc as required.
6.1 | 4 Module (White) with blank plate |  | 3 | Each | 491.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.1 | 4 Module (White) with blank plate | 3 | Each
6.2 | 6 Module (White) |  | 2 | Each | 564.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.2 | 6 Module (White) | 2 | Each
6.3 | 4 Module (Black) with blank plate |  | 9 | Each | 535.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.3 | 4 Module (Black) with blank plate | 9 | Each
6.4 | 6 Module (Black) |  | 20 | Each | 680.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.4 | 6 Module (Black) | 20 | Each
7 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate & swich box etc as required. | [53 empty] | 7 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate & swich box etc as required.
7.1 | 15/16A switch (Black) |  | 49 | Each | 257.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7.1 | 15/16A switch (Black) | 49 | Each
7.2 | 6 pin 15/16A socket (Black) |  | 49 | Each | 356 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7.2 | 6 pin 15/16A socket (Black) | 49 | Each
7.3 | 15/16A switch (white) |  | 9 | Each | 165.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7.3 | 15/16A switch (white) | 9 | Each
7.4 | 6 pin 15/16A socket (white) |  | 9 | Each | 209.47 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7.4 | 6 pin 15/16A socket (white) | 9 | Each
8 | Supplying and fixing of following modules GI box alongwith modular base & cover plate for modular switches in surface etc as required. | [53 empty] | 8 | Supplying and fixing of following modules GI box alongwith modular base & cover plate for modular switches in surface etc as required.
8.1 | 6Module |  | 1 | Each | 416.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 8.1 | 6Module | 1 | Each
9 | Fixing of 8/12 ways surface mounted vertical type 415V TPN MCB distribution board of sheet steel, dust protected duly powder painted inclusive of tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCbs (but without MCBs and incomer) as required. Note: (Legrand make Vertical DB shall be supplied by The Department at free of cost). |  | 1 | Each | 286.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 9 | Fixing of 8/12 ways surface mounted vertical type 415V TPN MCB distribution board of sheet steel, dust protected duly powder painted inclusive of tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCbs (but without MCBs and incomer) as required. Note: (Legrand make Vertical DB shall be supplied by The Department at free of cost). | 1 | Each
10 | Supplying and fixing 5A to 32A rating, 240/415V, 10kA, "C" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand | [53 empty] | 10 | Supplying and fixing 5A to 32A rating, 240/415V, 10kA, "C" curve single pole miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Make : Legrand
10.1 | Single pole |  | 24 | Each | 272.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 10.1 | Single pole | 24 | Each
11 | Supplying and fixing following rating four pole 415V residual current circuit breaker (RCCB), having a sensitivity current of 30mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand | [53 empty] | 11 | Supplying and fixing following rating four pole 415V residual current circuit breaker (RCCB), having a sensitivity current of 30mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. Note: DB Make - Legrand
11.1 | 40A |  | 1 | Each | 3389.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 11.1 | 40A | 1 | Each
12 | Supplying and fixing following rating four pole 415V miniature circuit breaker (MCB) 'C' curve, in the existing MCB DB/Enclosure complete with connections, testing and commissioning etc. as required. Note: DB/Enclosure Make - Legrand | [53 empty] | 12 | Supplying and fixing following rating four pole 415V miniature circuit breaker (MCB) 'C' curve, in the existing MCB DB/Enclosure complete with connections, testing and commissioning etc. as required. Note: DB/Enclosure Make - Legrand
12.1 | 32A |  | 1 | Each | 1631.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 12.1 | 32A | 1 | Each
13 | Supplying and fixing 32A 4P MCB and 40A,30mA 4P RCCB in sheet steel enclosure on surfcae complete with connections, testing and commissioning etc as required, |  | 2 | Each | 5336.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 13 | Supplying and fixing 32A 4P MCB and 40A,30mA 4P RCCB in sheet steel enclosure on surfcae complete with connections, testing and commissioning etc as required, | 2 | Each
14 | Supply of pre-fabricated powder coated Raceway (2.4Mtrs in length) with 14SWG(2mm) thickness CRCA sheet including the modular accessories as listed below: 1. 6/16A socket - 4Nos 2. 16A switch 4Nos 3. 6Module cover plate - 2Nos 4. 1M Cover plate - 6Nos Ensure Separate compartment for CAT 6 cable & Electrical Wire and seperate cut out for providing 6 numbers of LAN socket. Interconnection between sockets shall be done by using 3Rx 4Sq.mm FRLS PVC insulated copper wire. Drawing of the enclsoure shall be got approved from the department before fabrication. Make: Switches/Sockets/LAN Sockets - MK Blenze |  | 1 | Each | 7734.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 14 | Supply of pre-fabricated powder coated Raceway (2.4Mtrs in length) with 14SWG(2mm) thickness CRCA sheet including the modular accessories as listed below: 1. 6/16A socket - 4Nos 2. 16A switch 4Nos 3. 6Module cover plate - 2Nos 4. 1M Cover plate - 6Nos Ensure Separate compartment for CAT 6 cable & Electrical Wire and seperate cut out for providing 6 numbers of LAN socket. Interconnection between sockets shall be done by using 3Rx 4Sq.mm FRLS PVC insulated copper wire. Drawing of the enclsoure shall be got approved from the department before fabrication. Make: Switches/Sockets/LAN Sockets - MK Blenze | 1 | Each
15 | Supply, Installation, Testing and Commissioning of Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn |  | 1 | Each | 11170 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 15 | Supply, Installation, Testing and Commissioning of Maintenance free Chemical Earth Electrodes complying with the latest version of IS 3043 / IEC / IEEE Specifications. The Earth Electrode shall be with 2 M long, 14 mm. dia high tensile strength, copper bonded Steel Rods coated with minimum 250 micron pure eletrolytic Copper. Soil enrichment compound in quantities not less than 15 Kgs shall be used and the Earth Pit shall be back-filled with good quality soil without any Stones / Granules / Sand etc. The Earth Station shall be provided with suitable clamp made of SS to connect rod with earth conductor, polypropylene & polyethylene earth electrode inspection chamber with heay duty cover. The dimension shall be 300mmx300mmx 300mm with a weight bearing capacity of 50KN. Make : OBO/Cape/Dehn | 1 | Each
16 | Supply and fixing 25mm x 3mm copper strip on surface with necessary FRP support including earth bench for connections etc as required. |  | 17 | Mtrs | 771.9 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 16 | Supply and fixing 25mm x 3mm copper strip on surface with necessary FRP support including earth bench for connections etc as required. | 17 | Mtrs
17 | Supply and laying 25mm x 3mm copper strip at 0.5 metre below ground as strip earth electrode including connection/terminating with nut,bolt, spring, washer etc. as required.(jointing shall be done by overlapping and two sets of brass nut bolt and spring washer spaced at 50mm) |  | 4 | Mtrs | 615.6 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 17 | Supply and laying 25mm x 3mm copper strip at 0.5 metre below ground as strip earth electrode including connection/terminating with nut,bolt, spring, washer etc. as required.(jointing shall be done by overlapping and two sets of brass nut bolt and spring washer spaced at 50mm) | 4 | Mtrs
18 | Supply and laying UTP 4pair CAT 6 LAN cable in the existing surface/recessed PVC conduit as required. | [53 empty] | 18 | Supply and laying UTP 4pair CAT 6 LAN cable in the existing surface/recessed PVC conduit as required.
18.1 | 1 run of cable |  | 385 | metre | 60.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 18.1 | 1 run of cable | 385 | metre
19 | Supplying & fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | [53 empty] | 19 | Supplying & fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
19.1 | 25mm |  | 283 | metre | 154.18 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 19.1 | 25mm | 283 | metre
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information