## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Modification of Circuit Breaker capacity in the MV panel of Substation-4 at IISER, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply, Installation, testing and commisioning of EDO type1000A, FP, 50kA, Air Circuit Breaker -1 Nos on outgoing side and all control accessories in existing 415V, 50Hz MV panel including necessary Busbar extension, control cabling, re painting of rusted part with existing colour,1000/5A class1, 15VA CT-3sets with all related works and as directed by Engineer in charge. Note ACB shall have ICs=100%ICu ACB shall have Microprocessor based protection relase, 240V Shunt release Closing coil volatge=240V All CTs shall be cast resin type All ACB outgoing spare wired contacts for ON/OFF and Trip shall be provided for scada communication. Make of ACB: L&T UW-MTX 3.5 cat no.UW110NFD22300 |  | 1 | each | 216571 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply, Installation, testing and commisioning of EDO type1000A, FP, 50kA, Air Circuit Breaker -1 Nos on outgoing side and all control accessories in existing 415V, 50Hz MV panel including necessary Busbar extension, control cabling, re painting of rusted part with existing colour,1000/5A class1, 15VA CT-3sets with all related works and as directed by Engineer in charge. Note ACB shall have ICs=100%ICu ACB shall have Microprocessor based protection relase, 240V Shunt release Closing coil volatge=240V All CTs shall be cast resin type All ACB outgoing spare wired contacts for ON/OFF and Trip shall be provided for scada communication. Make of ACB: L&T UW-MTX 3.5 cat no.UW110NFD22300 | 1 | each
2 | Dismantling,re-Installation, testing and commisioning of 800A, FP, 50kA, Air Circuit Breaker -1 Nos on outgoing side and all control accessories in existing 415V, 50Hz MV panel including necessary Busbar extension, control cabling, re-painting of rusted part with existing colour,fixing of CT, and all related works as directed by EIC. Note:CT shall be dismanlted from the existing ACB cubicle. |  | 1 | each | 8227 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Dismantling,re-Installation, testing and commisioning of 800A, FP, 50kA, Air Circuit Breaker -1 Nos on outgoing side and all control accessories in existing 415V, 50Hz MV panel including necessary Busbar extension, control cabling, re-painting of rusted part with existing colour,fixing of CT, and all related works as directed by EIC. Note:CT shall be dismanlted from the existing ACB cubicle. | 1 | each
3 | Dismantling,re-installation, testing and commisioning of 630A FP MCCB -1 Nos on outgoing side and all control accessories in existing 415V, 50Hz LT panel including Busbar extension, neccesary control wiring, re painting of rusted part with existing colour,fixing of CT, RYB indication lamps-3sets, MFM with RS485port, ON /OFF/Trip indications-3 sets, control mcbs etc and all related works as directed by EIC. Note:CT shall be dismanlted from the existing ACB cubicle. |  | 1 | each | 13605 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Dismantling,re-installation, testing and commisioning of 630A FP MCCB -1 Nos on outgoing side and all control accessories in existing 415V, 50Hz LT panel including Busbar extension, neccesary control wiring, re painting of rusted part with existing colour,fixing of CT, RYB indication lamps-3sets, MFM with RS485port, ON /OFF/Trip indications-3 sets, control mcbs etc and all related works as directed by EIC. Note:CT shall be dismanlted from the existing ACB cubicle. | 1 | each
Total in Figures | [11 empty] | 1 | [39 empty] | #VALUE! | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information