## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: External Solar Street lighting along the road to Lecture Hall Complex and Physical Science Block at IISER, Thiruvananthapuram.
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply,installation, testing and commissioning of Smart Integrated hybrid Solar Street Light with built in mono crystalline panel, Lithium Ferro Phospate battery, MPPT Charge Controller and PIR Sensor with 2 Days Autonomy and Dimming Profile on existing octagonal pole as required. Luminaire shall comply with techical specification as below:- 1. Solar panel : Minimum not less than 60W & not greater than 75W +/-7W monocrystalline type 2. PIR sensor 3. IP 65 4. LED lamp life: 50000 Hrs 5. Battery : Lithium Ferro Phospate Battery or Lithium ION 6. Charge controller: MPPT with efficiency >= 90% 7. CRI: > 70 8. LED lumens: Minimum 6000lumens 9. Lumen efficiency: Minimum 150 Lumen/W 9. Colour Temperature 5700-6500K 10. Autonomy: 2 days 11. Working temperature: -10 deg C to +55 deg C 12. Height of installation: 6-7 meter 13. Hybrid switch: Inbuilt Model: Bajaj/Philips /Havells |  | 19 | Each | 48684.4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply,installation, testing and commissioning of Smart Integrated hybrid Solar Street Light with built in mono crystalline panel, Lithium Ferro Phospate battery, MPPT Charge Controller and PIR Sensor with 2 Days Autonomy and Dimming Profile on existing octagonal pole as required. Luminaire shall comply with techical specification as below:- 1. Solar panel : Minimum not less than 60W & not greater than 75W +/-7W monocrystalline type 2. PIR sensor 3. IP 65 4. LED lamp life: 50000 Hrs 5. Battery : Lithium Ferro Phospate Battery or Lithium ION 6. Charge controller: MPPT with efficiency >= 90% 7. CRI: > 70 8. LED lumens: Minimum 6000lumens 9. Lumen efficiency: Minimum 150 Lumen/W 9. Colour Temperature 5700-6500K 10. Autonomy: 2 days 11. Working temperature: -10 deg C to +55 deg C 12. Height of installation: 6-7 meter 13. Hybrid switch: Inbuilt Model: Bajaj/Philips /Havells | 19 | Each
2 | Supply and installation of 6mtr high hot dip galvanised octagonal poles with 130 mm bottom A/F & 70 mm top A/F made up of 3mm thick HR steel sheet along with base plate of size 200X200X12mm thick along with fully galvanised M20x600mm foundation bolts on reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) or as per the drawing recommended by the pole manufacturer including excavation, refilling, finishing etc. and with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, GI sheet for connecting cable gland, earthing etc as required.(Make: Transrail/Bajaj/Crompton/RR ISPAT) |  | 19 | Each | 26382.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Supply and installation of 6mtr high hot dip galvanised octagonal poles with 130 mm bottom A/F & 70 mm top A/F made up of 3mm thick HR steel sheet along with base plate of size 200X200X12mm thick along with fully galvanised M20x600mm foundation bolts on reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) or as per the drawing recommended by the pole manufacturer including excavation, refilling, finishing etc. and with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, GI sheet for connecting cable gland, earthing etc as required.(Make: Transrail/Bajaj/Crompton/RR ISPAT) | 19 | Each
3 | Supply of FRLS XLPE power cable of 1.1 kV grade of following size as required.(Make: Polycab/ Gloster/Havells/CCI) | [53 empty] | 3 | Supply of FRLS XLPE power cable of 1.1 kV grade of following size as required.(Make: Polycab/ Gloster/Havells/CCI)
3.1 | 3C x 6 sqmm Aluminium armoured cable (A2XFY) |  | 425 | Metre | 181.7 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3.1 | 3C x 6 sqmm Aluminium armoured cable (A2XFY) | 425 | Metre
4 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.(ISI make) | [53 empty] | 4 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.(ISI make)
4.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) |  | 360 | Metre | 263 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 360 | Metre
5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC HUME/ METAL/DWC HDPE pipe as required. | [53 empty] | 5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC HUME/ METAL/DWC HDPE pipe as required.
5.1 | Upto 35 sq. mm |  | 425 | Metre | 39 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.1 | Upto 35 sq. mm | 425 | Metre
6 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required. | [53 empty] | 6 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required.
6.1 | 3core X 6 sq. mm(19mm) |  | 40 | Each | 256 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6.1 | 3core X 6 sq. mm(19mm) | 40 | Each
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information