## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: Electrical works for providing additional electrical requirements & Dedicated Earthing in PSB B201 at IISER TVM campus, Vithura
Contact No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit/UPVC Trunking as required. | [53 empty] | 1 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit/UPVC Trunking as required.
1.1 | 3 x 2.5 sq. mm |  | 5 | Metre | 197 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.1 | 3 x 2.5 sq. mm | 5 | Metre
1.2 | 3 x 4 sq. mm |  | 220 | Metre | 297 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.2 | 3 x 4 sq. mm | 220 | Metre
1.3 | 3 x 6 sq. mm |  | 60 | Metre | 438 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.3 | 3 x 6 sq. mm | 60 | Metre
1.4 | 6 x 6 sq. mm |  | 34 | Metre | 862 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.4 | 6 x 6 sq. mm | 34 | Metre
2 | Supplying and fixing of following sizes of medium class PVC/flexible conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | [53 empty] | 2 | Supplying and fixing of following sizes of medium class PVC/flexible conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
2.1 | 25 mm |  | 105 | Metre | 209 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.1 | 25 mm | 105 | Metre
2.2 | 32 mm |  | 36 | Metre | 265 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2.2 | 32 mm | 36 | Metre
3 | Supplying and fixing of following sizes of UPVC Cable Management System/Mini Trunking System along with accessories on surface including supply of fixing materials, interconnecting clamps,bends,end caps, joint covers, internal and external corners, dividers, fixing screws as required | [53 empty] | 3 | Supplying and fixing of following sizes of UPVC Cable Management System/Mini Trunking System along with accessories on surface including supply of fixing materials, interconnecting clamps,bends,end caps, joint covers, internal and external corners, dividers, fixing screws as required
3.1 | 25mm x 12mm |  | 10 | Metre | 82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3.1 | 25mm x 12mm | 10 | Metre
3.2 | 100mm x 50mm |  | 17 | Metre | 967 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3.2 | 100mm x 50mm | 17 | Metre
4 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | [53 empty] | 4 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
4.1 | 300 mm width X 50 mm depth X 1.6 mm thickness |  | 10 | Metre | 1120 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 4.1 | 300 mm width X 50 mm depth X 1.6 mm thickness | 10 | Metre
5 | Supplying and fixing following modular switch/ socket/Blanking plate on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | [53 empty] | 5 | Supplying and fixing following modular switch/ socket/Blanking plate on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
5.1 | 6 A switch |  | 6 | Each | 148 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.1 | 6 A switch | 6 | Each
5.2 | 1 Module blanking plate (white/black) |  | 6 | Each | 58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 5.2 | 1 Module blanking plate (white/black) | 6 | Each
6 | Supplying and fixing suitable size GI/CMS box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. (White colour for normal power supply and Black colour for UPS power supply) |  | 25 | Each | 688 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6 | Supplying and fixing suitable size GI/CMS box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. (White colour for normal power supply and Black colour for UPS power supply) | 25 | Each
7 | Supplying and fixing suitable size GI/CMS box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. White colour for normal power supply and Black colour for UPS power supply) |  | 8 | Each | 845 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7 | Supplying and fixing suitable size GI/CMS box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. White colour for normal power supply and Black colour for UPS power supply) | 8 | Each
8 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. |  | 4 | Each | 125 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 8 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | 4 | Each
9 | Supplying and fixing following Modular base & cover plate on existing modular metal/PVC/CMS boxes etc. as required. | [53 empty] | 9 | Supplying and fixing following Modular base & cover plate on existing modular metal/PVC/CMS boxes etc. as required.
9.1 | 1or 2 Module |  | 5 | Each | 192 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 9.1 | 1or 2 Module | 5 | Each
10 | Supplying and fixing following size/ modules, PVC surface /CMS box on existing wall as required. | [53 empty] | 10 | Supplying and fixing following size/ modules, PVC surface /CMS box on existing wall as required.
10.1 | 1or 2 Module |  | 5 | Each | 198 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10.1 | 1or 2 Module | 5 | Each
11 | Supplying and fixing 32 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 32 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. |  | 2 | Each | 3124 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 11 | Supplying and fixing 32 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 32 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each
12 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 40 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required. |  | 1 | Each | 1685 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 12 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 40 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | 1 | Each
13 | Supplying and fixing 32 A, 415 V, TPN Industrial type socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 32 A "C" curve, FPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. |  | 2 | Each | 6240 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 13 | Supplying and fixing 32 A, 415 V, TPN Industrial type socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 32 A "C" curve, FPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each
14 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | [53 empty] | 14 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
14.1 | Single pole |  | 10 | Each | 369 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 14.1 | Single pole | 10 | Each
14.2 | Triple pole |  | 2 | Each | 1452 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 14.2 | Triple pole | 2 | Each
15 | Supply, Installation ,Testing, Commissioning of Light fittings, complete with all accessories (connectors etc) including connections etc. as required and all related works as directed by EIC. | [53 empty] | 15 | Supply, Installation ,Testing, Commissioning of Light fittings, complete with all accessories (connectors etc) including connections etc. as required and all related works as directed by EIC.
15.1 | 4 feet dimmable type surface led battern type light fittings , CCT-6500K, Luminous flux-min-2000 (Make-Philips smart Wi-Fi LED Tube light 24 W /Wipro/Crompton or Equivalent, Warranty-1 year) |  | 3 | Each | 1254 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 15.1 | 4 feet dimmable type surface led battern type light fittings , CCT-6500K, Luminous flux-min-2000 (Make-Philips smart Wi-Fi LED Tube light 24 W /Wipro/Crompton or Equivalent, Warranty-1 year) | 3 | Each
15.2 | 15W Recess type Round dimmable type Led light , CCT-6500K, Luminous flux-min-1500 . (Make-Philips Wiz Neo Smart Wifi LED Downlight 15W /Wipro/Crompton or Equivalent, Warranty-1 year) |  | 2 | Each | 2456 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 15.2 | 15W Recess type Round dimmable type Led light , CCT-6500K, Luminous flux-min-1500 . (Make-Philips Wiz Neo Smart Wifi LED Downlight 15W /Wipro/Crompton or Equivalent, Warranty-1 year) | 2 | Each
16 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with Earth enhancing mineral (20 Kg) as required as per IS 3043. Earth enhancing mineral compound is used for improving the soil conductivity. Earth enhancing mineral compound shall be so designed and constructed that in normal use their performance is reliable and without danger to persons and the surroundings. The material shall be mineral inert to sub soil and shall not pollute the environment. It shall provide a stable environment in terms of physical and chemical properties and exhibit low resistivity. It shall not be corrosive to the earth electrode itself. The material should have a resistivity less than 0.2 Ohm meter. It should be free from hazardous substances |  | 2 | Set | 21870 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 16 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with Earth enhancing mineral (20 Kg) as required as per IS 3043. Earth enhancing mineral compound is used for improving the soil conductivity. Earth enhancing mineral compound shall be so designed and constructed that in normal use their performance is reliable and without danger to persons and the surroundings. The material shall be mineral inert to sub soil and shall not pollute the environment. It shall provide a stable environment in terms of physical and chemical properties and exhibit low resistivity. It shall not be corrosive to the earth electrode itself. The material should have a resistivity less than 0.2 Ohm meter. It should be free from hazardous substances | 2 | Set
17 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm) |  | 12 | Metre | 1401 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 17 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm) | 12 | Metre
18 | Supplying and laying 25 mm X 3 mm copper strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm) |  | 19 | Metre | 875 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 18 | Supplying and laying 25 mm X 3 mm copper strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required.(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm) | 19 | Metre
19 | Providing and fixing 25 mm X 3 mm copper strip on surface or in recess for connections etc. as required. Note The strip shall be covered with green insulated sleeve |  | 57 | Metre | 1108 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 19 | Providing and fixing 25 mm X 3 mm copper strip on surface or in recess for connections etc. as required. Note The strip shall be covered with green insulated sleeve | 57 | Metre
20 | Supply, laying and fixing of PVC insulated and FRLS round sheathed annealed bare copper conductor industrial flexible cable of 1.1kV grade of following size on Surface/cable tray with suitable GI saddle including glanding and lugging (termination) as required. | [53 empty] | 20 | Supply, laying and fixing of PVC insulated and FRLS round sheathed annealed bare copper conductor industrial flexible cable of 1.1kV grade of following size on Surface/cable tray with suitable GI saddle including glanding and lugging (termination) as required.
20.1 | 6Cx 6Sq.mm Cu industrial flexible FRLS cable |  | 15 | Metre | 718 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 20.1 | 6Cx 6Sq.mm Cu industrial flexible FRLS cable | 15 | Metre
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information