## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.1 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Project Engineer cum Estate Officer(I/C), IISER Thiruvananthapuram
Name of Work: External Street lighting along the road at the rear side of Visitors Forest Retreat and at the rear side of Residence Area Children’s park at IISER, Thiruvananthapuram
Contract No: 04712778039/8036
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Rate in Figures to be entered by the bidder in Rs. p | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes Rs. P | TOTAL AMOUNT | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 7 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 8 | 9 | 10
1 | Supply, installation, testing and commissioning of pre-wired LED post top lanterns consisting of lumen level not less than 3300lumens and not more than 45W power, the fixture should be powder coated diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 3000K warm white,min 4KV surge protection, IP65 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required. (Approved Makes: Bajaj Cat No: ARIAN,Havells Cat No: RUBY,Philips BDP102 LED50/830 DS,KLITE KL-4523 Romania) |  | 32 | Each | 6543 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1 | Supply, installation, testing and commissioning of pre-wired LED post top lanterns consisting of lumen level not less than 3300lumens and not more than 45W power, the fixture should be powder coated diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 3000K warm white,min 4KV surge protection, IP65 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required. (Approved Makes: Bajaj Cat No: ARIAN,Havells Cat No: RUBY,Philips BDP102 LED50/830 DS,KLITE KL-4523 Romania) | 32 | Each
2 | Supply, installation, testing and commissioning of pre-wired LED post top lantern with glare free indirect lighting consisting of lumen level not less than 3300lumens and not more than 45W power, the fixture should be powder coated diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 4000K neutral white,min 4KV surge protection, IP65 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required. (Approved Makes: Bajaj Tenco BRIL,Havells Spirng6,,KLITE KL-4520 Gema) |  | 2 | Each | 9008 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Supply, installation, testing and commissioning of pre-wired LED post top lantern with glare free indirect lighting consisting of lumen level not less than 3300lumens and not more than 45W power, the fixture should be powder coated diecast aluminium housing with clear diffuser, THD<10%, PF>=0.95, 4000K neutral white,min 4KV surge protection, IP65 protection, conforms to IS 10322 Part 5 complete, including necessary interconnections and Earthing as required. (Approved Makes: Bajaj Tenco BRIL,Havells Spirng6,,KLITE KL-4520 Gema) | 2 | Each
3 | Supply and installation of 4mtr high hot dip galvanised conical poles with 118 mm bottom dia & 75 mm top dia made up of 3mm thick HT steel sheet along with base plate of size 200X200X12mm thick along with foundation bolts and suitable reducer to mount the light fixture as mentioned in item no. (1) on reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation (as per the drawing attached) including excavation, refilling, finishing etc. and with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, GI sheet for connecting cable gland, earthing etc as required. Make: Bajaj/RR ISPAT/Transrail |  | 32 | Each | 28140 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supply and installation of 4mtr high hot dip galvanised conical poles with 118 mm bottom dia & 75 mm top dia made up of 3mm thick HT steel sheet along with base plate of size 200X200X12mm thick along with foundation bolts and suitable reducer to mount the light fixture as mentioned in item no. (1) on reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation (as per the drawing attached) including excavation, refilling, finishing etc. and with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, GI sheet for connecting cable gland, earthing etc as required. Make: Bajaj/RR ISPAT/Transrail | 32 | Each
4 | Supply and installation of 4mtr high hot dip galvanised conical poles on the existing foundation with 118 mm bottom dia & 75 mm top dia made up of 3mm thick HT steel sheet along with base plate of size 200X200X12mm thick with suitable reducer to mount the light fixture as mentioned in item no. (1) and with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, GI sheet for connecting cable gland, earthing etc as required. Make: Bajaj/RR ISPAT/Transrail |  | 2 | Each | 19685 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 4 | Supply and installation of 4mtr high hot dip galvanised conical poles on the existing foundation with 118 mm bottom dia & 75 mm top dia made up of 3mm thick HT steel sheet along with base plate of size 200X200X12mm thick with suitable reducer to mount the light fixture as mentioned in item no. (1) and with 6A DP MCB , 3core x 1.5sqmm flexible PVC copper cable for interconnecting light fixture to the MCB, GI sheet for connecting cable gland, earthing etc as required. Make: Bajaj/RR ISPAT/Transrail | 2 | Each
5 | Supply & fixing of copper bonded ground rod having min 100 micron of copper coating, diameter of min 14.2 mm with length 600 mm driven into earth with necessary interconnections from pole foundation to earth rod using min 600mm length 10swg Cu. wire. All the interconnections shall be done using stainless steel nut bolts. |  | 34 | Each | 346 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 5 | Supply & fixing of copper bonded ground rod having min 100 micron of copper coating, diameter of min 14.2 mm with length 600 mm driven into earth with necessary interconnections from pole foundation to earth rod using min 600mm length 10swg Cu. wire. All the interconnections shall be done using stainless steel nut bolts. | 34 | Each
6 | Supply of FRLS XLPE power cable of 1.1 kV grade of following size as required. | [53 empty] | 6 | Supply of FRLS XLPE power cable of 1.1 kV grade of following size as required.
6.1 | 4C x 6 sqmm Aluminium armoured cable (A2XFY) |  | 600 | Metre | 346 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 6.1 | 4C x 6 sqmm Aluminium armoured cable (A2XFY) | 600 | Metre
7 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | [53 empty] | 7 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. Direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
7.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) |  | 510 | Metre | 263 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 7.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 510 | Metre
8 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC HUME/ METAL/DWC HDPE pipe as required. | [53 empty] | 8 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC HUME/ METAL/DWC HDPE pipe as required.
8.1 | Upto 35 sq. mm |  | 590 | Metre | 39 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 8.1 | Upto 35 sq. mm | 590 | Metre
9 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall surface as required. | [53 empty] | 9 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall surface as required.
9.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) |  | 35 | Metre | 58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 9.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 35 | Metre
10 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required. | [53 empty] | 10 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1kV grade as required.
10.1 | 4core X 6 sq. mm(19mm) |  | 66 | Each | 256 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 10.1 | 4core X 6 sq. mm(19mm) | 66 | Each
Total in Figures | [51 empty] | 0 | #REF! | INR Zero Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information